Project Name			Project #

PREFUNCTIONAL CHECKLIST

AIR HANDLING UNIT / COLD DECK

Location			Test #

Make 					Model#

Submittal / Approvals

Submittal.  All components of the work being installed have been submitted, reviewed and approved for use on this project. The components are complete and ready for prefunctional testing. Prior performance has been verified as complying with the contract documents as attested by the appropriate Contractor / Subcontractor signatures below. This prefunctional checklist is submitted for approval / witness, subject to an attached list of outstanding items yet to be completed. Any outstanding items will require completion before approval of this form can be executed. None of the outstanding items preclude safe and reliable prefunctional tests being performed.

___ List attached.

Mechanical Contractor		Date		Controls Contractor		Date

Electrical Contractor		Date		Plumbing Contractor		Date

Other Contractor		Date		General Contractor		Date

Prefunctional checklist items are to be completed as part of installation verification, preparatory to functional testing.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- Items that do not apply shall be noted with the reasons on this form (N/A = not applicable, BO = by others).

- Items on this checklist are to be verified by the Contractor as meeting the performance criteria of the contract documents before contacting Owner to witness.

MOTOR/ELECTRICAL:

Motor Manufacturer: 		Serial #

Motor Nameplate Data - 	Volt		FLA		HP

RMP		SVC Factor		Class		Frame

Actual per phase 	Volt		FLA

Starter Size		Fuse Size		Heater Size

| Approved | Cont. | UTH. |
| --- | --- | --- |
| INSTALLATION |  |  |
| Manufacturer’s cut sheets |  |  |
| Performance data |  |  |
| Installation and startup manual and plan |  |  |
| Shop drawings |  |  |
| INSTALLATION |  |  |
| Unit pressure leakage and deflection verified (report attached) |  |  |
| Permanent labels affixed, including for fans |  |  |
| Casing condition good: no dents, leaks, door gaskets installed |  |  |
| Access doors close tightly - no leaks |  |  |
| Boot between duct and unit tight and in good condition |  |  |
| Vibration isolation equipment installed & released |  |  |
| Maintenance access acceptable for unit and components |  |  |
| Sound attenuation installed |  |  |
| Thermal insulation properly installed and according to specification |  |  |
| Instrumentation installed according to specification (thermometers, pressure gages, flow meters, etc.) |  |  |
| Clean up of equipment completed per contract documents |  |  |
| Filters installed and construction filters in place |  |  |
| Valves, Piping and Coils properly installed and flushed (reports attached) |  |  |
| PolyChain or Vee Belt: Belt |  |  |
| Sheave size/number ________________________ |  |  |
| Bearings lubricated |  |  |
| SSTL lube lines installed |  |  |
| Alignment check: Fan sheave to motor sheave: degrees (0° ± 0°) |  |  |
| Fan wheel to shaft-all bolts torque checked |  |  |
| Interior lights and light switch operational |  |  |
| Pipes properly labeled |  |  |
| Pipes properly insulated |  |  |
| Strainers in place and clean |  |  |
| Chilled water lines counter-flow connection verified |  |  |
| All coils are clean and fins are combed |  |  |
| All condensate drain pans clean and slope to drain, per spec |  |  |
| Valves properly labeled |  |  |
| OSAT, MAT, SAT, RAT, chilled water supply sensors properly located and secure (related OSAT sensor shielded) |  |  |
| Sensors calibrated (report attached) |  |  |
| P/T plugs and isolation valves installed per drawings |  |  |
| Supply fan and motor alignment correct |  |  |
| Supply fan belt tension & condition good |  |  |
| Supply fan protective shrouds for belts in place and secure |  |  |
| Supply fan area clean |  |  |
| Supply fan and motor properly lubricated |  |  |
| Smoke and fire dampers installed properly per contract docs |  |  |
| All dampers close tightly |  |  |
| All damper linkages have minimum play |  |  |
| Low limit freeze stat sensor located to deal with stratification & bypass |  |  |
| Sound attenuators installed |  |  |
| No apparent severe duct restrictions |  |  |
| Turning vanes in square elbows as per drawings |  |  |
| OSA intakes located away from pollutant sources & exhaust outlets |  |  |
| Ducts cleaned as per specifications |  |  |
| Electrical and Controls |  |  |
| Pilot lights are functioning |  |  |
| Power disconnects in place and labeled |  |  |
| All electric connections tight |  |  |
| Proper grounding installed for components and unit |  |  |
| Safeties in place and operable |  |  |
| Starter overload breakers installed and correct size |  |  |
| Sensors calibrated (report attached) |  |  |
| Control system interlocks hooked up and functional |  |  |
| Smoke detectors in place |  |  |
| All control devices, pneumatic tubing and wiring complete |  |  |
| VFD connected and operational (report attached) |  |  |

Installation/application Rejected: The installation/application has not met the specified performance criteria and will require reinspection before approval.

Owner’s Representative / Commissioning Authority			Date

Approval: This filled-out checklist has been reviewed. Its completion is approved with the exceptions noted

Owner’s Representative / Commissioning Authority	Date