Project Name			Project #

PREFUNCTIONAL CHECKLIST

Variable Frequency Drive

Location			Test #

Make 					Model#

Submittal / Approvals

Submittal.  All components of the work being installed have been submitted, reviewed and approved for use on this project. The components are complete and ready for prefunctional testing. Prior performance has been verified as complying with the contract documents as attested by the appropriate Contractor / Subcontractor signatures below. This prefunctional checklist is submitted for approval / witness, subject to an attached list of outstanding items yet to be completed. Any outstanding items will require completion before approval of this form can be executed. None of the outstanding items preclude safe and reliable equipment testing and operation.

___ List attached.

Mechanical Contractor		Date		Controls Contractor		Date

Electrical Contractor		Date		Plumbing Contractor		Date

Other Contractor		Date		General Contractor		Date

Prefunctional checklist items are to be completed as part of installation verification, preparatory to functional testing.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- Items that do not apply shall be noted with the reasons on this form (N/A = not applicable, BO = by others).

- Items on this checklist are to be verified by the Contractor as meeting the performance criteria of the contract documents before contacting Owner to witness.

| VFD Information |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Make |  |  |  |  | Model Number |  |
| Serial Number |  |  |  |  | Service Area |  |
| Volts/Phase |  |  |  |  | Function |  |
| Motor HP |  |  | Motor Amps |  | Drive Max Amps |  |
| Comments: |  |  |  |  |  |  |

| Associated Checklists |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Cooling Tower |  | Air Handling Unit |  | Exhaust Fan |  |
| Pump |  | BAS |  | Other |  |
| Comments: |  |  |  |  |  |

| Requested documentation submitted | Rec’d |  | Comments |
| --- | --- | --- | --- |
| Manufacturer’s cut sheets |  |  |  |
| Performance data (pump curves, coil data, etc.) |  |  |  |
| Installation and startup manual and plan |  |  |  |
| O&M manuals |  |  |  |
| Factory test results |  |  |  |
| Sequences and control strategies |  |  |  |
| Warranty Certificate |  |  |  |
| Comments: |  |  |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| General |  |  |  |
| Installation per manufacturer's requirements |  |  |  |
| Permanent label affixed and UL stamp approved |  |  |  |
| Drive location not subject to excessive moisture or dirt |  |  |  |
| Drive location not subject to excessive temperatures |  |  |  |
| Appropriate Volts vs. Hz curve is being used |  |  |  |
| Drive size matches motor size |  |  |  |
| Drive independently mounted |  |  |  |
| Cooling air flow path clean and unobstructed |  |  |  |
| VFD interlocked to control system |  |  |  |
| Unit is programmed with full written programming record on site |  |  |  |
| Accel time set to __________ and Decel time set to __________ |  |  |  |
| Coordinated with BAS for all interface ranges and signal isolation |  |  |  |
| Restart on Power Failure parameter set to auto |  |  |  |
| Drive min and max speed set to ______ Hz min and 60 Hz max |  |  |  |
| Security settings set per owner direction and Password documented for owner |  |  |  |
| Drive response to loss of signal set to __________ |  |  |  |
| Output pulse resolution set to _________ MHz. (This is coordinated with the application to minimize audible noise and coordinated with driven bearing allowances.) |  |  |  |
| Input of motor FLA represents 100% to 105% of motor FLA rating |  |  |  |
| Upper frequency limit set at 100%, unless explained otherwise |  |  |  |
| Electrical and Controls |  |  |  |
| Power disconnect is located within site of the unit it controls and labeled |  |  |  |
| All electric connections tight |  |  |  |
| Grounding installed for components and unit |  |  |  |
| Safeties installed and operational |  |  |  |
| Overload breakers installed and correct size |  |  |  |
| All control devices and wiring complete |  |  |  |
| Control system interlocks connected and functional |  |  |  |
| Installation per manufacturer’s instructions |  |  |  |
| Rotates in the correct direction (for VFD, check Inverter and BYPASS modes) |  |  |  |
| Checked the input voltage with drive disconnected |  |  |  |

| Operational Checks |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| Operation checked in HAND, OFF, and AUTO. As applicable operation also checked in BYPASS. Where applicable, ensure safeties are active in all modes |  |  |  |
| Specified sequences of operation and operating schedules have been provided with all variations documented |  |  |  |
| Specified point-to-point checks have been completed and documentation record submitted for this system |  |  |  |
| Start-up complete |  |  |  |

Sensor and Actuator Calibration

Exceptions Noted:

All field-installed sensors and gages, and all actuators (dampers and valves) on this piece of equipment shall be calibrated in accordance with Specification Section 01810.  All test instruments shall have had a certified calibration within the last 12 months:  Y/N______.  Sensors installed in the unit at the factory with calibration certification provided need not be field calibrated.

| Sensor or Actuator Tag & Location | Location OK | 1st Gage or BAS Value | Instrument Measured Value | Final Gage or BAS Value | Pass Y / N |
| --- | --- | --- | --- | --- | --- |

Installation/application Rejected: The installation/application has not met the specified performance criteria and will require reinspection before approval.

Owner’s Representative / Commissioning Authority			Date

Approval: This filled-out checklist has been reviewed. Its completion is approved with the exceptions noted

Owner’s Representative / Commissioning Authority	Date