Project Name			 Project #

FUNCTIONAL TEST CHECKLIST

PLUMBING FIXTURE TEST

Location			Test #

Submittal / Approvals

Submittal.  All components of the work being installed have been submitted, reviewed and approved for use on this project. The system is complete and ready for functional testing. All associated prefunctional checklists are complete, approved and attached to this FT. Prior performance has been verified as complying with the contract documents as attested by the appropriate Contractor / Subcontractor signatures below.. Any outstanding items are noted as requiring correction / completion on attached list. Any outstanding items will require completion before approval of this form can be executed. None of the outstanding items preclude safe and reliable functional tests being performed.

___ List attached.

Mechanical Contractor		Date		Controls Contractor		Date

Electrical Contractor		Date		Plumbing Contractor		Date

Other Contractor		Date		General Contractor		Date

Functional checklist items are to be completed and approved before placing equipment into operation.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- Items that do not apply shall be noted with the reasons on this form (N/A = not applicable, BO = by others).

- Tests performed with this FT are to be verified by the Contractor as meeting the performance criteria of the contract documents before contacting Owner to witness.

Hot Water system operational verification procedures:

  - Adjust hot water heater temperature to 115° F.

  - Adjust and set balance valves on each floor for each zone.

  - Upon completion, shut off all fixtures (no flow), and allow system to stabilize for 24 hours.

  - After 24 hours, beginning with the lowest floor, and the fixtures furthest from that zones balancing valve; turn on hot water and record the amount of time the water reaches operating temperature.

  - Complete report for that fixture and continue to the next fixture and repeat step 4.

Pressure reading at circulation pump is:					PSI.

Fixture operational verification procedure:

Sinks

1.Place stopper over/in drain basket.

2. Fill sink 2-3 inches with water using hot and cold valves.

3. Verify no leaks at valves / supply lines

4. Removed stopper and verify no leaks at drain lines

Restroom Fixtures

- Operate valves at fixtures to ensure water hammer arrestor operational.

- Ensure automatic flush valve operation

Emergency / Standard Shower

- Operate valves and ensure proper flow

- Verify no leaks

| Fixture Location | Time to reach Temp (sec.) | Water Flow | No Leaks | Cont. | UTH. |
| --- | --- | --- | --- | --- | --- |

Test Failure/Retest Required: The Test performed has not met the specified performance criteria and will require retesting before approval.

Owner’s Representative / Commissioning Authority			Date

Approval: The test has been witnessed as meeting the performance requirements of the contract documents with any exceptions noted.

Owner’s Representative / Commissioning Authority	Date