Project Name			 Project #

FUNCTIONAL TEST CHECKLIST

PUMP

Location			Test #

Submittal / Approvals

Submittal.  All components of the work being installed have been submitted, reviewed and approved for use on this project. The system is complete and ready for functional testing. All associated prefunctional checklists are complete, approved and attached to this FT. Prior performance has been verified as complying with the contract documents as attested by the appropriate Contractor / Subcontractor signatures below.. Any outstanding items are noted as requiring correction / completion on attached list. Any outstanding items will require completion before approval of this form can be executed. None of the outstanding items preclude safe and reliable functional tests being performed.

___ List attached.

Mechanical Contractor		Date		Controls Contractor		Date

Electrical Contractor		Date		Plumbing Contractor		Date

Other Contractor		Date		General Contractor		Date

Functional checklist items are to be completed and approved before placing equipment into operation.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- Items that do not apply shall be noted with the reasons on this form (N/A = not applicable, BO = by others).

- Tests performed with this FT are to be verified by the Contractor as meeting the performance criteria of the contract documents before contacting Owner to witness.

| Approved | Cont. | UTH. |
| --- | --- | --- |
| Record Submittal |  |  |
| O&M Manuals |  |  |
| Sequence of Operations verified |  |  |
| OPERATION |  |  |
| VFD operation verified (report attached) |  |  |
| The HOA switch properly activates and deactivates the unit |  |  |
| Pump rotation verified correct |  |  |
| No unusual noise or vibration |  |  |
| No leaking apparent around fittings |  |  |
| Measure line to line voltage phase imbalance for each pump: (%Imbalance = 100 x (avg. - lowest) / avg.) |  |  |
| Record imbalance of each pump (report attached) |  |  |
| Record full load running amps for each pump. _____rated FL amps x ______srvc factor = _______ (Max amps) |  |  |
| Specified sequences of operation and operating schedules have been implemented with all variations documented |  |  |
| Specified point-to-point checks have been completed and documentation record submitted for this system |  |  |
| Pump speed. Check the amperage of the circulating pumps. Amperage should be less than the rated amps. Rated = ________ SP-1[_____] SP-2[_____] |  |  |
| Change the schedule so the pumps should be OFF. Pumps turn OFF. |  |  |
| Schedule the pumps to be ON. Return schedule to normal. Pumps start. Schedule returned to normal |  |  |

Sensor and Actuator Calibration

All field-installed pressure sensors and gages on this piece of equipment shall be calibrated using the methods and tolerances given in the Calibration and Leak-by Test Procedures document.

All test instruments shall have certified calibration during past 12 months:  Y/N____.

Sensors installed in the unit at the factory with calibration certification provided need not be field calibrated.

| Sensor or Actuator & Location | Loc-ation OK | 1st Gage or BAS Value | Instr. Meas’d Value | Final Gage or BAS Value | Pass Y/N? |
| --- | --- | --- | --- | --- | --- |

Gage reading = reading of the permanent gage on the equipment. BAS = building automation system. Instr. = testing instrument.  Visual = actual observation. The Contractor’s own sensor check-out sheets may be used in lieu of the above, if the same recording fields are included and the referenced procedures are followed.

Test Failure/Retest Required: The Test performed has not met the specified performance criteria and will require retesting before approval.

Owner’s Representative / Commissioning Authority			Date

Approval: The test has been witnessed as meeting the performance requirements of the contract documents with any exceptions noted.

Owner’s Representative / Commissioning Authority	Date