Project Name			 Project #

FUNCTIONAL TEST CHECKLIST

SUMP PUMP

Location			Test #

Submittal / Approvals

Submittal.  All components of the work being installed have been submitted, reviewed and approved for use on this project. The system is complete and ready for functional testing. All associated prefunctional checklists are complete, approved and attached to this FT. Prior performance has been verified as complying with the contract documents as attested by the appropriate Contractor / Subcontractor signatures below.. Any outstanding items are noted as requiring correction / completion on attached list. Any outstanding items will require completion before approval of this form can be executed. None of the outstanding items preclude safe and reliable functional tests being performed.

___ List attached.

Mechanical Contractor		Date		Controls Contractor		Date

Electrical Contractor		Date		Plumbing Contractor		Date

Other Contractor		Date		General Contractor		Date

Functional checklist items are to be completed and approved before placing equipment into operation.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- Items that do not apply shall be noted with the reasons on this form (N/A = not applicable, BO = by others).

- Tests performed with this FT are to be verified by the Contractor as meeting the performance criteria of the contract documents before contacting Owner to witness.

| Approved | Cont. | UTH. |
| --- | --- | --- |
| DELIVERABLES |  |  |
| Record Submittal |  |  |
| Performance data |  |  |
| Service / maintenance contract |  |  |
| Sequences and control strategies |  |  |
| O&M manuals |  |  |
| PERFORMANCE |  |  |
| The HOA switch properly activates and deactivates the unit |  |  |
| Pump rotation verified correct |  |  |
| Vibration within tolerances (report attached) Y / N |  |  |
| Verify noise dB within tolerances |  |  |
| No leaking apparent around fittings |  |  |
| Measure line to line voltage phase imbalance for each pump: (%Imbalance = 100 x (avg. - lowest) / avg.) Imbalance :_______________________ |  |  |
| Record full load running amps for each pump. _____rated FL amps x ______srvc factor = _______ (Max amps) |  |  |
| Specified sequences of operation and operating schedules have been implemented and verified (report attached) Y / N |  |  |
| Specified point-to-point checks have been completed (report attached) Y / N |  |  |
| VFD operation verified (report attached) Y / N |  |  |
| High level alarm operates |  |  |
| Float switch operates |  |  |
| Discharge location verified |  |  |

Test Failure/Retest Required: The Test performed has not met the specified performance criteria and will require retesting before approval.

Owner’s Representative / Commissioning Authority			Date

Approval: The test has been witnessed as meeting the performance requirements of the contract documents with any exceptions noted.

Owner’s Representative / Commissioning Authority	Date