Texas State Fire Marshal’s Office

P. O. Box 149221,  MC: 112-FM           Austin, Texas   78714-9221

	Contractor's Material and Test Certificate for Underground Piping
	

	PROCEDURE

Upon completion of work, inspection and tests shall be made by the contractor’s representative and witnessed by an owner’s representative.  All defects shall be corrected and system left in service before contractor’s personnel finally leave the job.

A certificate shall be filled out and signed by both representatives.  Copies shall be prepared for approving authorities, owners, contractor, and the State Fire Marshal.  It is understood the owner’s representative’s signature in no way prejudices any claim against contractor for faulty material, poor workmanship, or failure to comply with approving authority’s requirements or local ordinances.

	Property Name 
	Date 

	Property Address 
	City 
	State 
	Zip 

	PLANS
	Accepted by approving authorities (names) 

	
	Address 

	
	Installation conforms to accepted plans
(
Yes
(
No

Equipment used is approved
(
Yes
(
No

If no, state deviations


	INSTRUCTIONS
	Has person in charge of fire equipment been instructed as to location of

control valves and care and maintenance of this new equipment?
(
Yes
(
No

If no, explain



	
	Have copies of appropriate instructions and care and maintenace

charts been left on premises?
(
Yes
(
No

If no, explain

	LOCATION


	Supplies buildings
	 

	UNDERGROUND PIPES AND JOINTS


	Pipe types and class 


	Type joints 



	
	Pipe conforms to 
 

Standard
(
Yes
(
No

Fittings conform to
 

Standard
(
Yes
(
No 

If no, explain 

	
	Joints needed anchorage clamped, strapped or blocked in 
(
Yes
(
No

accordance with _________________ standard

If no, explain

	TEST DESCRIPTION
	FLUSHING:  Flow the required rate until water is clear as indicated by no collection of foreign material in burlap bags at outlets such as hydrants and blow-offs.  Flush at flows not less than 390 GPM (1476 L/min) for 4-inch pipe, 880 GPM (3331 L/min) for 6-inch pipe, 1560 GPM (5905 L/min) for 8-inch pipe, 2440 GPM (9235 L/min) for 10-inch pipe, and 3520 GPM (13323 L/min) for 12-inch pipe. When supply cannot produce stipulated flow rates, obtain maximum available.

HYDROSTATIC:  Hydrostatic tests shall be made at not less than 200 psi (13.8 bars) for two hours or 50 psi (3.4 bars) above static pressure In excess of 150 psi (10.3 bars) for two hours.

LEAKAGE:  New pipe laid with rubber gasketed joints shall, if the workmanship is satisfactory, have little or no leakage at the joints.  The amount of leakage at the joints shall not exceed 2 quarts per hour (1.89 L/hr) per 100 joints irrespective of pipe diameter.  The leakage shall be distributed over all joints.  If such leakage occurs at a few joints, the installation shall be considered unsatisfactory and necessary repairs made.  The amount of allowable leakage specified above can be increased by 1 fl oz per inch valve diameter per hour (30 mL/25 mm/hr) for each metal seated valve isolating the test section.  If dry barrel hydrants are tested with the main valve open so the hydrants are under pressure, an additional 5 oz per minute (150 mL/min) leakage is permitted for hydrant.

	
	New underground piping flushed according to_________________ standard by (company)
(
Yes
(
No

If no, explain 

	FLUSHING
	How flushing flow was obtained
(
Public water
(
Tank or reservoir
(
Fire pump
	Through what type of opening

(
Hydrant butt
    (
Open pipe

	TESTS
	Lead-ins flushed according to _______________ standard by (company)
(
Yes
(
No

If no, explain 



	
	How flushing flow was obtained
(
Public water
(
Tank or reservoir
(
Fire pump
	Through what type of opening
(
Y connection to flange spigot
     (
Open pipe


	HYDROSTATIC TEST
	All new underground piping hydrostatically tested at

 

psi
for
 

hours
	Joints covered

(
Yes
(
No

	LEAKAGE

TEST
	Total amount of leakage measured


 

gallons
 

hours

	
	Allowable leakage


 

gallons
 

hours

	HYDRANTS
	Number installed 


	Type and make 


	All operate satisfactorily

(
Yes
(
No

	CONTROL VALVES
	Water control valves left wide open
(
Yes
(
No

If no, state reason

Hose threads of fire department connections and hydrants interchangeable with those of

the fire department answering alarm
(
Yes
(
No

	REMARKS
	Date left in service  



	Signature


	Name of installing contractor
	C  of  R  No.     SCR-



	
	Contractor’s Address
	City
	State
	Zip

	
	Tests witnessed by

	
	For property owner (signed)
Title 
Date 

	
	For Installing contractor (signed)
Title
Date 

	Additional explanation and notes

	
	

	
	I certify that the information herein is true and that this portion of the sprinkler system was installed in accordance with Article 5.43-3, Texas Insurance Code and the rules and standards adopted by the State Fire Marshal’s Office.

	RME
	Responsible Managing Employee (signature) 

	CERTIFICATION
	Responsible Managing Employee (print or type name) 

	
	RME License Number 
	Date 


DISTRIBUTION:
Original COPY 1 posted at site.    
COPY 3 for approving authority.  


COPY 2 for the installing firm.

COPY 4 for the Texas State Fire Marshal’s Office.

SF042 Rev. 09/05                                                       Contractor’s Material and Test Certificate for Underground Piping                                                   Page 1 of 2


