SECTION 07565                      
    PREPARATION FOR REROOFING

01/07

UTHealth FPE Standard Specification
SECTION 07 22 16

ROOF BOARD INSULATION

This Standard Specification Section is controlled by the Office of Facilities Planning and Construction, The University of Texas System.  It is to be used as guideline on all UT System projects, unless deviations are approved in writing by the Project Manager.  It is not to be used for bidding, permitting, construction or any other purpose.  This document is the property of UT System, and use of this document, in part or in whole, for any purpose other than for a UT System project may not be done without written permission of UT System.

To receive current updates of standard specification sections, please go to the web site at: www.utsystem.edu/fpc or contact the Office of Facilities Planning and Construction. 

The issuance and revision history of this section is tabulated below.  Unless contractually required for another UT System project, please destroy any previous copy in your possession.

	Rev No.
	Date
	Pages
	Remarks

	0
	January 2007
	11
	Issuance 

	
	
	
	

	
	
	
	

	
	
	
	


UTHealth FPE Standard Specification
SECTION 07 22 16

ROOF BOARD INSULATION

Hidden Text (will not print) - Specifier Note: There are numerous types of roof insulation, some which are installed in multiple-layer roof assemblies.  Specifier to verify specific Project requirements related to roof deck, drainage, fire resistance, wind uplift, surfacing, logistics and other items. 

Do not incorporate this Section in Project Manual if an alternate method of providing roof insulation is utilized – such as insulating concrete roof deck system 
This Section does not include vapor retarder or air-barriers.  A/E to determine  vapor retarder or air barrier requirements, and consult with OFPC Project Manager.  Coordinate incorporation of these products into, or referenced in this Section if these products are required.
PART 1   GENERAL

1.01 SECTION INCLUDES Verify scope .
A. Roof Insulation
B. Roof Insulation Fasteners and Adhesive

C. Tapered Insulation

D. Tapered Edge

1.02 RELATED WORK Verify related Sections titles and names.
A. Section 06 10 00 - Rough Carpentry

B. Section 07 51 13 –Built-Up Asphalt Roofing

C. Section 07 52 00 – Modified Bituminous Membrane Roofing
D. Section 07 62 00 - Sheet Metal Flashing and Trim
1.03 REFERENCES Verify appropriate reference standards  Typically wind loads are determined by using the  American Society of Civil Engineers - Minimum Design Loads for Buildings and Other Structures (ASCE 7 – verify version) document.  Verify special wind zone requirements, such as coastal.  .
A. National Roofing Contractors Association (NRCA) Roofing and Waterproofing Manual
B. Underwriters Laboratories (UL) 

1. Roofing Materials and Systems Directory

2. Fire Resistance Directory
C. ASTM D41 - Asphalt Primer Used in Roofing

D. ASTM D312 - Asphalt Used in Roofing Use if hot asphalt is used in roof system.  This specification includes hot asphalt as an adhesive for attaching second layer of roof insulati
E. ASTM C 728 - Perlite Thermal Insulation Board

F. ASTM C 1289 - Faced Rigid Cellular Polyisocyanurate Thermal Insulation Board

Below ASTM Standards are listed for information only – delete the below ASTM listings if not used.  This Specification does not include products listed by these standards.  If a particular Project requires a different type of roof insulation consult OFPC Manager for prior review.
G. ASTM C 208 - Cellulosic Fiber Insulating Board

H. ASTM C 552 -  Cellular Glass Thermal Insulation

I. ASTM C 578 - Rigid, Cellular Polystyrene Thermal Insulation

J. ASTM C 726 -  Mineral Fiber Roof Insulation Board

K. ASTM C 984 - Perlite Board and Rigid Cellular Polyisocyanurate Composite Roof Insulation

1.04 SUBMITTALS 
A. Submit under provisions of SPECIAL CONDITIONS requirements and Division 1 Section 01 21 00 Submittal Procedures. Verify Division 1 Section number reference and submittal requirements. 
B. Prior to pre-roofing meeting, submit the following:

1. Manufacturer's Certification:  Letter from manufacturer, on letterhead, and signed by authorized representative that roof insulation meets requirements for required warranties and is compatible with roof membrane products. 

2. Product Literature:  Submit product literature on roof system and accessory components.  
C. Asphalt Fume Control Plan:  Submit equipment data, and proposed loading and heating procedures to limit ground-level asphalt fumes. Verify need for fume control depending on site location, Owner preference, and roof insulation adhesive type
D. Shop Drawings: Submit shop Drawings for approval prior to Pre-roofing Conference and start of Work.  Include the following Drawings: Certain Projects may require a detailed Shop Drawing submittal.  Below requirements illustrate a comprehensive approach to Shop Drawings. 
1. Roof Plan(s):  
a) Include on roof plan tapered insulation locations at field, perimeter, and roof curbs.  Indicate insulation thickness at high and low points, crickets pattern, and drain or scupper sumps.

b) Outline roof dimensions, including all levels.

2. Provide scaled insulation attachment plan for each roof area indicating perimeter and corner requirements to achieve specified wind uplift resistance.  Provide insulation fastening pattern Drawing for corner, perimeter, and field zones.  

E. Product data:

1. Insulation products:  Submit manufacturer’s data sheets for each component required including insulation boards, adhesives, fasteners, plates and bitumen or adhesive.  Provide roofing system manufacturer’s written acceptance of proposed insulation board, adhesives, fasteners, and procedures for installation.  Coordinate with roof membrane Specification Section(s). Verify Section number.
2. Material Safety Data Sheets:  Provide manufacturer’s MSDS information for all materials proposed for use.

3. Provide evidence of specified fire and wind uplift ratings for proposed insulation.
4. ASTM Compliance Sheet:  Submit product material list with corresponding ASTM standard(s) each product complies with.  Include Specification paragraph reference number that relates to each product.
1.05 QUALIFICATIONS

A. Installer:  Company specializing in performing the Work of this Section and approved by roof manufacturer for installation of specified roof system.

B. Minimum 5 years documented successful experience with installation of products specified in this Section.

1.06 REGULATORY REQUIREMENTS

A. Fire Resistance: 
1. UL Class A Fire Hazard Classification. Roof insulation is an integral component in the UL tested assemblies.  Insulation is tested with roof membranes at specific slopes.  Verify insulation, in combination with roof deck and membrane assembly meets UL Class A.  
2. UL _______ Roof Ceiling Assembly Rating.  Verify roof ceiling assembly rating requirements for particular Project– NR, 1 hour, 2 hour, etc  Roof insulation is an integral component in the UL tested assemblies.  Certain UL assemblies are specific to size, thickness, type and other insulation properties.  Several tested assemblies require the use of accessory products, such as gypsum board.   Recommend inclusion (or reference) of accessory products in this Section if accessory products are required.
1.07 TOLERANCES

A. Comply with tolerances listed in this Section.

B. Where tolerances are not expressly stated in these Specifications, or by the manufacturer, perform Work within tolerances specified in the NRCA Roofing and Waterproofing Manual.

1.08 PRE-ROOFING CONFERENCE
A. Schedule meeting to discuss roof Work before start of Work onsite. 
B. Comply with requirements of roof membrane Specification Section(s).
1.09 DELIVERY, STORAGE, AND HANDLING

A. Deliver, store, and handle products according to manufacturer's recommendations.

B. Deliver products in original containers, dry, undamaged, with seals and labels intact.

C. Storage: Verify particular jobsite conditions as related to material storage.
1. Roof-top storage of weather-sensitive material is not permitted.  Material stored overnight on roof-top will be considered defective.

2. Note – Select ONE of the following statements:-If site conditions allow storage trailers onsite use the following.Store weather-sensitive products in enclosed storage trailers. 
Or if site conditions do not allow storage trailers 
Store weather-sensitive products on pallets, clear of ground, and cover with secure breathable canvas tarps. 
 Or if site conditions do not allow site storage 
Store weather-sensitive products in an enclosed warehouse, or in storage trailers off-site.  Deliver products in quantity that can be used each day, without roof-top storage.  Products must be returned to warehouse, or storage trailer, each day.
D. Store related materials within temperature ranges recommended by the manufacturer(s) of each product.

1.010 ENVIRONMENTAL REQUIREMENTS

A. Comply with manufacturer’s environmental requirements for storage and application of products.

B. Verify existing and forecasted weather conditions and determine when conditions are acceptable for roof Work within the guidelines as follows:

1. Do not proceed with Work when ambient air temperature falls below 40˚ F.

2. Do not proceed with roof application when excessive moisture is present.  Excessive moisture is that which may be detected by sight or touch, or that which results in visible foaming of hot asphalt.

C. Do not expose materials sensitive to water, or sunlight, damage in quantities greater than can be weatherproofed during each day.

1.011 COORDINATION

A. Coordinate Work with installation of associated metal flashings as the Work of this Section proceeds.

1.012 INSPECTION BY MANUFACTURER

A. Comply with requirements of roof membrane Specification Section(s).

B. Provide manufacturer's field inspection reports within five days of each site visit.

1.013 ROOF SYSTEM WARRANTY Verify Owner preferences for roof warranty.
A. Provide manufacturer's roof system warranty according to roof membrane Specification Section(s).
B. Warranty shall include coverage for roof insulation, either as part of original warranty language, or by attachment.  
1.014 INSTALLER WARRANTY

A. Roof Installer Warranty:  provide under provisions of Section 01 70 50 – Project Closeout. Verify Section number.
B. Coordinate with requirements of roof membrane Specification Section(s).

PART 2   PRODUCTS Verify Owner preferences and Project requirements for roof insulation assembly..
2.01 GENERAL

A. Roof Insulation:  Obtain written approval from roof membrane manufacturer for use of insulation products incorporated into roof system, which are not supplied by roof membrane manufacturer.

B. Substitutions:  
1. Where specific products are listed in this Specification, the referenced manufacturer’s systems are to establish a level of quality.  
2. Requests for substitutions to listed products shall be submitted during the bidding phase per requirements of Section 01 21 00.  Verify Section number.
3. Consideration of requests for substitution is at the sole discretion of the A/E and Owner, and approvals shall be issued in writing by the A/E with Owner concurrence.
2.02 BITUMINOUS MATERIALS

A. Asphalt Bitumen:  ASTM D312, Type IV, special steep, as supplied or specifically approved by membrane manufacturer. Verify hot bitumen use for roof insulation application.  Certain Projects may be sensitive to asphalt fumes (see fume control above) or limited access for asphalt kettle. Other means of insulation attachment are available.
B. Asphalt Primer:  ASTM D41, as supplied or specifically approved by insulation manufacturer.

2.03 INSULATION Verify insulation requirements to meet particular Project requirements.  Below two layers of 2.3 inch thick polyisocyanurate (4.6 inch thick insulation – plus thickness of coverboard) insulation assembly is designed to provide an approximate Long Term Thermal Resistance (LTTR) R-value of 30.  Also verify if other products are needed to meet required fire (gypsum board?) or other rating(s).
A. First Layers:  two (2) layers, 2.3 inch thick polyisocyanurate, non-organic fiberglass facers top and bottom, as supplied by, or approved by roof membrane manufacturer for use in their warranted roof system, mechanically fastened to roof deck. Verify attachment method, (type of roof deck dictates attachment method) thickness and number of layers of polyisocyanurate  
B. Insulation Fasteners:  ensure plates and screws meet wind uplift rating and warranty requirements.  Verify attachment method.  Screws and plates are typically used over metal decks.  Revise fastening method If particular Project has a different roof deck type.
1. Plates:  Galvalume-coated steel, in size, type, and configuration to meet uplift requirements.

2. Screws:  Stainless-steel or polymer-coated steel shank, meeting Factory Mutual 4470 corrosion-resistance.  Length sufficient to penetrate ¾ inch through top flute of roof deck.
C. Coverboard:  ASTM C728, one layer, 3/4 inch thick perlite, supplied, or recommended by roof membrane manufacturer, set in hot asphalt. Verify attachment method, and type of coverboard.  Perlite is listed here as coverboard, although other types of insulation, gypsum board or other material can provide an adequate top layer substrate.  Verify compatibility with roof membrane type, insulation value, attachment method and warranty provisions.
Roof Slope Note:  Above insulation is designed to be applied over a roof deck with structural slope.  Most low-sloped roofing systems require roof decks should slope  at 1/4 inch per foot slope-to-drain.  Slopes that exceed ¼ inch per foot should be reviewed to ensure compliance with maximum slope recommended by manufacturer and compliance with fire rating.  Typically a sloped roof deck is more economical than using tapered insulation to achieve slope. Use tapered insulation where roof deck does not provide positive slope-to drain.  Verify type and slope requirements for tapered insulation.  Indicate tapered roof insulation area(s) on roof plan(s).
2.04 TAPERED CRICKETS AND TAPERED EDGE Verify Project Requirements for these products.
A. Tapered Crickets: 

1. First course: ASTM C728, perlite tapered edge, minimum 12 inches wide, in thickness to match butt edge of tapered insulation, set in hot asphalt.

2. Remaining courses: ASTM C728, perlite, ½ inch per foot tapered, set in hot asphalt.  Verify attachment method and slope of tapered roof insulation required to provide positive slope-to-drain.  Typically ½ inch per foot tapered roof insulation is required to provide positive slope when installed on a roof deck sloped ¼ inch per foot.
B. Tapered Edge:  ASTM C728, perlite.  Provide in widths and thicknesses indicated on Drawings.
C. Roof Drain & Scupper Sumps: minimum 1½ inch to 0, 24” wide tapered perlite.

2.05 SPECIAL BITUMEN HEATING EQUIPMENT Verify Project Requirements for fume control
A. Provide ground-level filtering, or after-burning asphalt fume system equipment.

B. Equip kettle with carton loader device.

C. Ensure positive seals at kettle lid, loader, and piping, to ensure containment of ground-level asphalt fumes.

PART 3 – EXECUTION

3.01 GENERAL

A. Work of this Section shall be performed in accordance with quality workmanship standards as defined by NRCA.
B. The roof systems manufacturer’s technical specifications shall be considered a part of this Section and shall be used as a minimum standard in conjunction with this Section.  If this Section conflicts with, or exceeds manufacturer’s minimum requirements the more rigid standard shall apply and be enforced.

3.02 COORDINATION

A. Ensure proper sequencing of roof insulation and to allow installation of roof and flashings as detailed, without damage.

B. Coordinate activities to prevent damage to roof assemblies.

3.03 EXAMINATION & PREPARATION
A. Do not store, stage activities, or allow construction traffic over roof areas, unless protection plan is approved in advance by A/E.  

B. Contractor is responsible for maintaining insulation in good condition.

C. Verify that surfaces and site conditions are ready to receive Work.  Verify that debris has been completely removed from roof area and broom clean the deck immediately prior to insulation application.
D. Verify deck is clean, sound, smooth, and dry enough for covering with roof insulation.  Report decking not serviceable for covering with roof insulation.  Do not install finish application of roof insulation over unserviceable roof deck area(s).
E. Verify roof openings, curbs, pipes, sleeves, ducts, and vents through roof are solidly set, and wood components are in place.

F. Install nailers and blocking immediately prior to application of roof insulation.  

G. Construct and install nailers and blocking under provisions of Section 06 10 00. Verify Section number.
3.04 TEMPORARY WATERPROOFING

A. Provide water stops and temporary tie-ins daily to prevent moisture penetration into building interior or installed assemblies. 

B. Seal roofing temporarily to the deck where leakage could penetrate installed assemblies.  Remove upon resumption of Work.

C. Provide permanent, or temporary, counter flashing daily.

D. Install membrane assemblies complete with strip-in plies each day.  Use mastic seals only in such a manner that mastic does not remain between finished modified bitumen plies at cant strips and membrane terminations.  Provide seal at all terminations, both vertical and horizontal.
E. Provide temporary seals which do not soil finished Work surfaces or contaminate surfaces intended to receive sealants.

F. Remove temporary seals from completed Work.

3.05 BITUMEN HEATING  Verify hot bitumen use – see comments above
A. Comply with manufacturer’s requirements for heating, and applying bitumen.

B. Heat asphalt bitumen to achieve EVT at point of application, as stamped on asphalt carton, plus or minus 25˚ F.

C. Use insulated tubing and luggers during cold weather to maintain correct temperature at the point of application.  

D. Verify accurate temperature readings at point of application to ensure compliance.  Establish proper temperature at kettle, hold time on roof, and substrate type and temperature to achieve proper application temperature.  

E. Measure temperature periodically, minimum one reading every two hours or when conditions change.  Contractor to provide accurate temperature measuring device for verification.

F. Adjust temperature, equipment, or procedure to maintain proper application temperature.
G. Do not heat bitumen above finished blowing temperature for more than 3 hours, unless bitumen is under continuous use.

H. Provide fume control equipment to minimize asphalt fumes during the Work.  Comply with fume control requirements of this Specification and submitted Fume Control Plan. Verify need for fume control depending on site location, Owner preference, and system type
3.06 APPLICATION IN COLD WEATHER

A. Comply with manufacturer's special recommendations for membrane application during cold weather.

B. Discontinue installation if asphalt temperature cannot be maintained at EVT at point of application.

3.07 INSULATION APPLICATION- GENERAL

A. Apply insulation in accordance with insulation and insulation and membrane manufacturer's recommendations.  

B. Install so that boards are in moderate and continuous contact with adjacent boards, but not jammed or forced.

C. Ensure that starter row is straight.  Realign boards if perceptible gaps or spaces occur.  Fill ¼ inch and greater gaps with loose perlite insulation before covering.

D. Cut individual boards if necessary, to conform to humps or depressions in deck.  Miter edges to prevent open joints at penetrations, Projections, and terminations.

E. Install boards with joints staggered in the cross direction. 

F. Protect installed insulation from damage and moisture infiltration.

3.08 First Layer(s) Insulation Application Verify roof deck type.  Below application is for direct application to a metal deck.  Other roof decks will require alternate means of installation, and require editing of below requirements.  The use of gypsum board over a metal deck to achieve a specific fire rating would require editing the below information.
A. Position boards to ensure bottom board edges bear on top flange of metal deck, minimum 1 inch, at areas where board is directly over metal deck.  Cut, and realign boards which do not bear sufficiently on top flange of metal deck.  

B. Stagger board joints from gypsum board joints minimum 6 inches in both directions, where insulation is installed over gypsum board.

C. Install boards with joints staggered in the cross direction.

D. Fasten first layer insulation with screw and plates to metal deck.  Ensure fasteners engage top of deck flute, and penetrate deck minimum 3/4 inch.

E. Ensure screws engage deck properly.  Remove unengaged screws and reposition new screws to engage deck.

3.09 Second Layer Insulation Application Verify top layer insulation type and attachment.
A. Set second layer insulation into full bed of asphalt over first layer insulation.  

B. Install one layer cover board over first layer insulation where roof deck is sloped.
C. Install tapered insulation over first layer insulation in areas where roof deck is not sloped.  Verify tapered insulation requirements.
D. Stagger joints, minimum 6 inches, in both directions, from first layer insulation.  Remove and replace insulation with improper staggering of joints.

E. Step-in each board, while asphalt is still molten, to ensure full embedment.

F. Set loose, cut boards, at overnight tie-ins, to provide uninterrupted staggering of insulation joints, upon resumption of Work.

3.010 APPLICATION OF TAPERED EDGE 

A. Apply tapered edge into solid moppings of asphalt and step in completely.  

B. Make straight, neat cuts and miter corners without perceptible gaps, or open joints.

C. Stagger joints minimum 6 inches between layers.

D. Cut, shave, modify and combine various sized tapered materials, to provide smooth, uniform transitions.

E. Install 1.5 inch to 0 inch, 2 foot square tapered edge at scupper and 4 foot square roof drain sumps. Verify sump requirements.
3.011 PROTECTION 

A. Protect stored insulation prior to installation according to provisions of this Section.  Do not install improperly stored materials into the Work.

B. Cover roof insulation with waterproof roof membrane daily.  Install according to roof membrane Specification Section(s).
C. Do not expose roof insulation overnight.  Remove and replace roof insulation exposed overnight.
D. Remove and replace roof insulation that has been wetted, damaged or is otherwise unserviceable.

E. Include removal and replacement of wet roof insulation in roof membrane warranty.
END OF SECTION
AUSTECH ROOF CONSULTANTS INC.

COPYRIGHT 1990                                            07565-12
	Roof Board Insulation

07 22 16 - Page 12 of 12

	



