SECTION 07565                      
    PREPARATION FOR REROOFING

01/07


UTHealth FPE Standard Specification
SECTION 07 62 00
SHEET METAL FLASHING AND TRIM
This Standard Specification Section is controlled by the Office of Facilities Planning and Construction, The University of Texas System.  It is to be used as guideline on all UT System projects, unless deviations are approved in writing by the Project Manager.  It is not to be used for bidding, permitting, construction or any other purpose.  This document is the property of UT System, and use of this document, in part or in whole, for any purpose other than for a UT System project may not be done without written permission of UT System.

To receive current updates of standard specification sections, please go to the web site at: www.utsystem.edu/fpc or contact the Office of Facilities Planning and Construction. 

The issuance and revision history of this section is tabulated below.  Unless contractually required for another UT System project, please destroy any previous copy in your possession.

	Rev No.
	Date
	Pages
	Remarks

	0
	January 2007
	13
	Issuance 

	
	
	
	

	
	
	
	

	
	
	
	


UTHealth FPE Standard Specification
SECTION 07 62 00
SHEET METAL FLASHING AND TRIM
Hidden Text (will not print) - Specifier Note: There are numerous types of sheet metal flashing.  Specifier to verify specific Project requirements related to roof type, drainage, wind uplift, corrosion-resistance, ascetics, logistics and other items. 

This Section does not include vapor retarder or air-barriers.  A/E to determine vapor retarder or air barrier requirements, and consult with OFPC Project Manager.  Coordinate incorporation of these products into, or referenced in this Section if these products are required.
PART 1   GENERAL

1.01 SECTION INCLUDES Verify scope.
A. Sheet metal flashings

B. Gutters and downspouts

C. Collectorheads

1.02 RELATED WORK Verify related Sections titles and names.
A. Section 06 10 00 - Rough Carpentry

B. Section 07 31 13 – Asphalt Shingle Roofing

C. Section 07 32 13 – Clay Roof Tile

D. Section 07 41 13 – Metal Roof Panels

E. Section 07 51 13 – Asphalt Built-Up Roofing

F. Section 07 52 00 – Modified Bituminous Roofing
G. Section 07 92 00 – Joint Sealants

1.03 REFERENCES Verify appropriate reference standards   Verify special wind zone requirements, such as coastal.
A. SMACNA - Architectural Sheet Metal Manual, 2003 Edition

B. ASTM A167 - Stainless and Heat-Resisting Chromium‑Nickel Steel Plate

C. ASTM A653 - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process
D. ASTM A792 - Standard Specification for Steel Sheet, 55% Aluminum-Zinc Alloy-Coated by the Hot-Dip Process
E. ASTM B32 - Solder Metal

F. ASTM B209 - Aluminum and Aluminum-Alloy Sheet and Plate

G. ASTM B370 - Copper Sheet and Strip for Building Construction

H. Federal Specification FS 0-F-506 - Flux, Soldering, Paste, and Liquid

I. ANSI/SPRI ES-1 - Wind Design Standard for Edge Systems Used with Low Slope Roofing Systems Verify appropriate reference standard for roof edge sheet metal design and attachment.  International Building Code 2003 (§1504.5) lists ES-1 as perimeter flashing standard, with the caveat “except the basic wind speed shall be determined from Figure 1609”  Figure 1609 is the wind speed map of the United States.   .  
1.04 SUBMITTALS 
A. Submit under provisions of SPECIAL CONDITIONS requirements and Division 1 Section 01 21 00 Submittal Procedures. Verify Division 1 Section number reference and submittal requirements. 
B. Prior to pre-roofing meeting, submit the following:

1. Manufacturer's Certification:  document that certifies metal products meet requirements. 

2. Product Literature:  Submit product literature on sheet metal and accessory components.  
3. Perimeter Flashing Certification:  document that certifies roof perimeter edge sheet metal flashing meets ANSI/SPRI ES-1 Design Standard. Verify appropriate reference standard for roof edge sheet metal design and attachment.
C. Shop drawings: Submit shop drawings for approval prior to Pre-roofing Conference and start of Work.  Include the following Drawings: Certain Projects may require a detailed Shop Drawing submittal.  Below requirements illustrate a comprehensive approach to Shop Drawings. 
1. Indicate on Shop Drawings material profiles, jointing patterns, jointing details, fastening methods, and installation instructions.

2. Indicate location of sealants, tapes and gaskets.

3. Indicate material type, finish and gage.

D. Product data:

1. Sheet metal products:  Submit manufacturer’s data sheets for each material Coordinate with roof Specification Section(s). Verify Section number.
2. Material Safety Data Sheets:  Provide manufacturer’s MSDS information for all materials proposed for use.

3. ASTM Compliance Sheet:  Submit product material list with corresponding ASTM standard(s) each product complies with.  Include Specification paragraph reference number that relates to each product.
1.05 QUALIFICATIONS

A. Installer:  Company specializing in performing the work of this Section and approved by roof manufacturer for installation of specified roof system.

B. Minimum 5 years documented successful experience with installation of products specified in this Section.

1.06 REGULATORY REQUIREMENTS

A. Wind Uplift Resistance:  Perimeter sheet metal edge to comply with ANSI/SPRI ES-1.   Verify appropriate reference standard for roof edge sheet metal design and attachment.  International Building Code 2003 (§1504.5) lists ES-1 as perimeter flashing standard, with the caveat “except the basic wind speed shall be determined from Figure 1609”  Figure 1609 is the wind speed map of the United States… 
1.07 TOLERANCES

A. Comply with tolerances listed in this Section.

B. Where tolerances are not expressly stated in these Specifications, or by the manufacturer, perform Work within tolerances listed in the SMACNA Architectural Sheet Metal Manual.

1.08 PRE-ROOFING CONFERENCE
A. Schedule meeting to discuss roof Work before start of work onsite. 
B. Comply with requirements of roof Specification Section(s).
1.09 DELIVERY, STORAGE, AND HANDLING

A. Deliver, store, and handle products according to manufacturer's recommendations.

B. Deliver products in original containers, dry, undamaged, with seals and labels intact.

C. Storage: Verify particular jobsite conditions as related to material storage.
1. Roof-top storage of weather-sensitive material is not permitted.  Material stored overnight on roof-top will be considered defective.

2. Note – Select ONE of the following statements:-If site conditions allow storage trailers onsite use the following:Store weather-sensitive products in enclosed storage trailers. 
Or if site conditions do not allow storage trailers 
Store weather-sensitive products on pallets, clear of ground, and cover with secure breathable canvas tarps. 
 Or if site conditions do not allow site storage 
Store weather-sensitive products in an enclosed warehouse, or in storage trailers off-site.  Deliver products in quantity that can be used each day, without roof-top storage.  Products must be returned to warehouse, or storage trailer, each day.
D. Store related materials, within temperature ranges, recommended by the manufacturer(s) of each product.

E. Stack sheet metal to prevent twisting, bending, or abrasion, and to provide ventilation.  
F. Do not stack products on roof surfaces without properly securing to prevent blow-off and sliding-off roof. 
G. Slope metal sheets to ensure drainage

1.010 ENVIRONMENTAL REQUIREMENTS

A. Comply with manufacturer’s environmental requirements for storage and application of products.

B. Verify existing and forecasted weather conditions and determine when conditions are acceptable for roof Work within manufacturer’s recommended guidelines:

C. Do not expose materials sensitive to water, or sunlight, damage in quantities greater than can be weatherproofed during each day.

1.011 COORDINATION

A. Coordinate Work with installation of associated metal flashings as the Work of this Section proceeds.

1.012 INSPECTION BY MANUFACTURER

A. Comply with requirements of roof membrane Specification Section(s).

B. Provide manufacturer's field inspection reports within five days of each site visit.

1.013 MANUFACTURER WARRANTY Verify Owner preferences for inclusion of sheet metal flashing into roof warranty.  Roof manufacturers who provide sheet metal flashing may offer inclusion of sheet metal flashing in roof warranty.
A. Provide manufacturer's roof system warranty according to roof Specification Section(s).  Include sheet metal flashings provided by roof manufacturer for incorporation into their roof system.
B. Provide 20 year material warranty(s) for ASTM A792 and prefinished sheet metal coating(s).  
1.014 SUBSTITUTIONS  
A. Where specific products are listed in this Specification, the referenced manufacturer’s systems are to establish a level of quality.  

B. Requests for substitutions to listed products shall be submitted during the bidding phase per requirements of Section 01 21 00.  Verify Section number.
C. Consideration of requests for substitution is at the sole discretion of the A/E and Owner, and approvals shall be issued in writing by the A/E with Owner concurrence.

1.015 INSTALLER WARRANTY

A. Roof Installer Warranty:  provide under provisions of Section 01 70 50 – Project Closeout. Verify Section number.
B. Coordinate with requirements of roof membrane Specification Section(s).

PART 2   PRODUCTS Verify Owner preferences and Project requirements for sheet metal.
2.01 SHEET MATERIALS
A. Stainless Steel:  ASTM A167; 24 gauge sheet steel; Type 304; non-magnetic.

B. Copper Sheet Metal:  Sheet copper, ASTM B370, 16 ounce and 20 ounce.

C. Galvanized Sheet Metal:  Sheet steel, ASTM A653, G90 coating, in various gages.

D. Galvalume® Sheet Metal:  Sheet steel with aluminum-zinc alloy coating, ASTM A792, in various gauges.
E. Prefinished Sheet Metal:  Sheet steel, Galvalume according to ASTM A792, with full-strength Kynar 500 coating, 24 gauge, in color chosen by A/E. 
F. Aluminum Sheet and Plate:  ASTM B209, anodized color, form alloy, gage and temper appropriate for use, color chosen by A/E.

2.02 FASTENERS
A. Flashing Nails:  threaded nails; 

1. Non-Ferrous Metal:  non-magnetic stainless steel slater's nails, minimum 3/8 inch head.

2. Ferrous Metal:  hot-dipped galvanized; minimum 3/8 inch head.

B. Screws: thread design to meet application, add minimum 5/8 inch diameter EPDM integral washer where exposed to weather.

1. Non-Ferrous Metal: #12, non-magnetic stainless-steel screws.

2. Ferrous Metal:  #12, galvanized or polymer coating steel screw, with head designed to meet application.

C. Masonry Screws:  1/4 inch diameter, galvanized, with polymer finish; slotted hex washer head with minimum 5/8 inch EPDM washer; Tapcon by Buildex, or approved substitute.

D. Pop Rivets:  full stainless steel, including mandrel; in size to meet application.

E. Fastener lengths as required to penetrate:

1. Minimum 1 inch, maximum 1-1/2 inch into masonry

2. Minimum 1-1/4 inch, or through wood receiving members

3. Minimum 1/2 inch through sheet metal and steel receiving members

2.03 ACCESSORIES
A. Solder:  ASTM B32 - 50/50 type

B. Flux:  FS 0-F-506

C. Bituminous Products: According to provisions of membrane roofing Specification.

D. Sealants:  according to provisions of Section 07 92 00.  Verify Section number.
E. Sealant Tape: butyl tape, 100 percent solids, in width and thickness to meet application.

F. Roof Penetration Flashing Sealer:  ASTM C-920, Type S, Grade P, class 25, use TM; one-part self leveling polyurethane sealer.
G. Asphalt Primer:  ASTM D41, as supplied or specifically approved by insulation manufacturer.
PART 3 – EXECUTION

3.01 GENERAL

A. Work of this Section shall be performed in accordance with standards as defined in SMACNA Architectural Sheet Metal Manual.
B. The roof manufacturer’s technical specifications shall be considered a part of this Section and shall be used as a minimum standard in conjunction with this Section.  
C. If this Section conflicts with, or exceeds manufacturer’s minimum requirements the more rigid standard shall apply and be enforced.

3.02 COORDINATION

A. Coordinate installation of sheet metal components to ensure quality installation.

B. Strip-in metal flanges built into roof membrane daily.  Remove, and reinstall flanges left overnight.

C. Coordinate installation of through-wall flashings with masonry, and dampproofing, to achieve required quality.

D. Ensure proper sequencing to allow installation of roof and flashings as detailed, without damage.

E. Coordinate activities to prevent damage to adjacent surfaces.

3.03 EXAMINATION & PREPARATION
A. Do not store, stage activities, or allow construction traffic over roof areas, unless protection plan is approved in advance by A/E.  

B. Contractor is responsible for maintaining sheet metal and accessories in good condition during delivery, storage, installation and Final Completion.

C. Verify that surfaces and site conditions are ready to receive Work.  Verify that debris has been completely removed from roof area and broom clean immediately prior to sheet metal application.
D. Verify flashing substrate is clean, sound, smooth, and dry enough for covering.  Report substrate not serviceable.  Do not install finish application sheet metal over unserviceable area(s).
E. Verify roof openings, curbs, pipes, sleeves, ducts, and vents through roof are solidly set, and wood components are in place.

F. Ensure nailers and blocking are properly attached and ready for application of sheet metal.  

G. Construct and install nailers and blocking under provisions of Section 06 10 00. Verify Section number.
H. Field-measure site conditions prior to fabricating work.  Note variances; adjust dimensions to accommodate site conditions.

I. Pre-prime top surface of metal flanges which will be built-into roof membrane, except where field soldering is required.

J. Provide separation of dissimilar metals by back-painting concealed contact surfaces with asphalt primer, both surfaces.

3.04 TEMPORARY WATERPROOFING

A. Provide water stops and temporary tie-ins daily to prevent moisture penetration into building interior or installed assemblies. 

B. Seal roofing temporarily to the deck where leakage could penetrate installed assemblies.  Remove upon resumption of Work.

C. Provide permanent, or temporary, counter flashing daily.

D. Install membrane assemblies complete with strip-in plies each day.  Use mastic seals only in such a manner that mastic does not remain between finished modified bitumen plies at cant strips and membrane terminations.  Provide seal at all terminations, both vertical and horizontal.
E. Provide temporary seals which do not soil finished work surfaces or contaminate surfaces intended to receive sealants.

F. Remove temporary seals from completed Work.

3.05 FABRICATION

A. Fabricate flashings and components true to shape, accurate in size, square, and free from distortion or defect.

B. Ensure symmetrical layout of running lengths of sheet metal.

C. Fabricate corners, intersections and terminations of "running" flashing fixed as components, separate from other lengths of flashings.  Fabricate such components with maximum 18 inch legs.

D. Partially assemble sub-components of corner intersections, and termination components; set partially assembled components in place to verify fit and that each seats properly before soldering or joining the finished assembly.

E. Form a slight kick-down to edges of metal flanges to be built into roof membranes, maximum 1/4 inch wide, maximum 10 degree brake.

F. Hem exposed edges 1/2 inch.

G. Obtain prior approval from Engineer to adjust dimensions and configurations of sheet metal flashings, to allow more effective yield of material, or to facilitate fabrication.  Ensure that adjustments comply with design intent.

3.06 SOLDERING

A. Solder only fixed components, which have maximum 18 inch legs.  

B. Pre-tin both sides of edges to be soldered, using flux and solder to full anticipated width of joint.

C. Join sub-components together before soldering.  For flat seams, and whenever possible, form flat-lock seams, binding sheets tightly.  Where flat-lock seams are impractical, provide tabs, partially interlocked, if possible, and join with pop-rivets at 1 inch on center.

D. Do not solder over nail heads.

E. Apply flux to surface of joint, and solder slowly with well heated irons.  Heat sheets as necessary to sweat solder to full width of seam, or minimum 3/4 inch.  Ensure an even flow of solder without excess build-up.

F. Solder joints in a horizontal position whenever possible.  When soldering on slopes steeper than 45˚, apply a second bead, neatly laced.

G. Neutralize flux from surfaces immediately after soldering, using cloth saturated with 10% solution of washing soda and water, and wipe again using separate cloth and clean water.

3.07 JOINTING

A. Form joints in running flashings to accommodate thermal movement equally throughout all joints.

B. Provide "slip"-type joints each side of soldered or joined components, except where total length of intersecting lengths is less than 5 feet.

C. Provide joints aligned with joints in walls.  Overlap, notch, and loosely interlock adjoining sections at lower hem.  Fasten only one side of joint.

D. Form rigid, fixed joints only when constructing fixed components.  Provide minimum 3/4 inch tabs, interlocked where possible.  Join sections with tabs concealed.

E. Solder fixed joints in galvanized and stainless steel.  Rivet and seal fixed joints in prefinished sheet metal.

F. Expansion Joint Covers: apply two beads of concealed sealant, 6 inch lap, shingle fashion.

G. Counter Flashing:

1. Form minimum 3 inch lap joint.  Apply single bead of sealant, concealed inside lap.  Notch and interlock lower hem, allowing for 1/4 inch movement.  Do not fasten through lap.

2. Tab corners, seal between tabs with sealant (or solder corner) and rivet 1 inch on center.

3. Align, or add joints, to counter flashing at wall panel joints.

H. Concealed Continuous Cleats:  Leave 1/2 inch space between lengths.

I. Exposed Cleats:

1. Form minimum 3 inch lap joint.  Apply single bead of sealant, concealed inside lap.  Notch and interlock lower hem, allowing 1/4 inch movement.  Do not fasten through lap.

2. Tab corners, seal between tabs with sealant (or solder corner), and rivet 1 inch on center.

3.08 INSTALLATION

A. Comply generally with recommendations in the "Architectural Sheet Metal Manual", by SMACNA, except where otherwise specified.

B. Provide uniform, symmetrical layout of flashing sections, seams, joints, and fasteners.

C. Prime, and embed, sheet metal flanges built-into roof membrane in solid 1/8 inch bed of plastic cement.  Fasten to wood nailer 3 inches on center, in staggered pattern.  Apply strip-in plies on the same day.  

D. Roughen prefinish paint finish on metal flanges built into roof membrane, and apply primer.

E. Ensure proper fit and positioning of flashings.  Make adjustments necessary to accommodate variances and imperfections in receiving surfaces.

F. Install flashings free of warp or distortion, and without stress on fixed components.

G. Stagger joints between components.

3.09 GUTTERS

A. Fabricate from 10 foot lengths, except maximum 5 foot lengths at corners.

B. Install gutter straps 18 inches on center.  Fasten with rivets.

C. Rivet 1 inch on center between double beads at front, back and bottom.

D. Solder joints together. Install gutter expansion joint maximum 40 feet on center.

E. Miter, tab, rivet, and solder corners.  

3.010 DOWNSPOUTS

A. Fabricate downspout drops with minimum ¾ inch tabs and 4 inch long vertical section.  Solder drops together as a single unit.  

B. Insert drops through properly sized opening in floor of gutter.  Rivet and solder to floor of gutter.  Locate drops away from gutter joints.  Connect downspout to drop with rivets 2 inches on center.

C. Fabricate downspouts to 5 inch by 4 inch, with double-lock concealed seam.

D. Connect downspout sections together with 4 inch overlap and rivet sections together.

E. Fasten downspout to wall with 1 inch, wide straps spaced 5 feet on center.  

F. Fasten straps to wall and to downspout.  Locate straps to conceal downspout joints.

G. Install splash pan diverters where downspouts empty onto asphalt shingle roofing.

3.011 PROTECTION 

A. Protect stored sheet metal and accessories prior to installation according to provisions of this Section.  Do not install improperly stored materials into the Work.

B. Remove and replace sheet metal that has been water-stained, damaged or is otherwise unserviceable.

3.012 SCHEDULE  This Schedule is an example of one method to specify particular sheet metal items.  Verify actual sheet metal items, finish, gage, fastener and pattern and revise below Schedule to meet Project requirements.  Schedule is intended to provide Contractor necessary information for bidding and installation.  Delete below Schedule if A/E intends to include below information on Drawings or Specification text.  Include provisions for additional fastening at corners for roof edge metal and coping if ES-1 standard applies.  
	ITEM
	FINISH
	GAUGE
	FASTENER
	PATTERN

	Asphalt Shingle Roof Flashings
	
	
	
	

	Headwall Flashing
	Prefinished
	24
	Neoprene-Head Screw
	12 inches on center

	Step Shingles
	Galvanized
	24
	Threaded Nail
	1 each

	Counter Flashing
	Prefinished
	24
	Neoprene-Head Screw
	12 inches on center

	Soldered Curb Flashing
	Galvanized
	24
	Screws
	4 each

	   Cleat
	Galvanized
	22
	Threaded Nail
	12 inches on center

	Metal Roof and Siding Flashings
	
	
	
	

	Counter Flashing
	Prefinished
	24
	Screw
	12 inches on center

	Pocket Receiver
	Prefinished
	24
	Screw
	12 inches on center

	Ridge
	Prefinished
	24
	Neoprene-Head Screw
	6 inches on center

	Ridge Closure
	Galvanized
	16
	Neoprene-Head Screw
	6 inches on center

	Ridge Plate
	Galvanized (Prime & Paint)
	16
	Screw
	24 inches on center

	Gutter
	Prefinished
	24
	Wood Screw & Washer
	16 inches on center

	   Gutter Strap
	Galvanized
	18
	Rivets
	3 each strap

	   Outlet Tube
	Stainless Steel
	24
	Pop Rivets
	2 inches on center

	Downspouts
	Prefinished
	24
	Straps
	5 feet on center

	   Straps
	Prefinished
	24 (x2)
	Wall: Screw

Downspout:  Rivet
	one each side

one each side

	Zee Purlin at Eave
	Galvanized
	16
	Screws
	12 inches on center

	Eave Closure
	Galvanized
	16
	Screws
	4 each

	Eave Support Angle
	Galvanized
	16
	Screws
	12 inches on center

	Wall Panel Closure
	Galvanized
	22
	Screws
	12 inches on center

	Rake Flashing
	Prefinished
	24
	Neoprene-Head Screw
	12 inches on center

	Concealed Rake Support
	Galvanized
	16
	Screws
	12 inches on center

	Asphalt Built-Up Roof & Modified Bituminous Roof Flashings
	
	
	
	

	Counter Flashing
	Prefinished
	24
	Screw
	12 inches on center

	Pocket Receiver
	Prefinished
	24
	Screw
	12 inches on center

	Roof Drain Flashing
	Sheet Lead
	4 lb.
	Set in Plastic Cement
	Full bed

	Overflow Scupper Liner
	Copper
	16 oz
	Threaded Nail

Hem to Collectorhead
	3 inches on center

Continuous

	Scupper Face Plate
	Copper
	16 oz
	Hem to Scupper
	Continuous

	Scupper Counter Flashing
	Copper
	16 oz
	Screws
	16 inches on center or one each stud

	Termination Bar
	Alum.
	3/16”
	Screw
	12 inches on center

	Soldered Sheet Metal Hood
	Galvanized
	24
	Neoprene-Head Screw
	2 each

	Louver Counter Flashing
	Copper
	16 oz
	Clips
	12 inches on center

	Louver Counter Flashing Clips
	Copper
	20 oz
	Screws
	One each

	Louver Cover Plates

(Alternate No. 3)
	Copper
	16 oz
	Neoprene-Head Screw
	12 inches on center

	Clay Roof Tile Flashings
	
	
	
	

	Metal Edge
	Copper
	16 oz
	Threaded Nail

Hem to Cleat
	12 inches on center

Continuous

	Metal Edge Cleat
	Copper
	20 oz
	Threaded Nail
	12 inches on center

	Expansion Joint Cover
	Copper
	16 oz
	Neoprene-Head Screw

Cleat
	16 inches on center

Continuous 

	Expansion Joint Cleat
	Copper
	20 oz
	Neoprene-Head Screw
	16 inches on center

	Sheet Lead Flashing
	Lead (Prime & Paint)
	2.5 lb.
	Threaded Nail 

Embed in Mastic
	12 inches on center

Continuous

	Sidewall Flashing
	Copper
	16 oz
	Cleat
	12 inches on center

	Sidewall Cleat
	Copper
	20 oz
	Threaded Nail
	One each

	Valley Flashing
	Copper
	20 oz
	Cleat
	12 inches on center

	Valley Cleat
	Copper
	20 oz
	Threaded Nail
	One each

	Headwall Flashing
	Copper
	16 oz
	Cleat
	12 inches on center

	Headwall Clip
	Copper
	20 oz
	Screw
	One each

	Gutter
	Copper
	20 oz
	Wood Screw & Washer
	16 inches on center

	   Gutter Strap
	Copper Bar
	1/8”
	Rivets
	3 each strap

	   Outlet Tube
	Copper
	20 oz
	Rivets
	2 inches on center

	Downspouts
	Copper
	16 oz
	Straps
	5 feet on center

	   Straps
	Copper Bar
	1/8”
	Wall: Screw

Downspout:  Rivet
	one each side

one each side


END OF SECTION

AUSTECH ROOF CONSULTANTS INC.

COPYRIGHT 1990                                            07565-12
Sheet Metal Flashing and Trim
07 62 00 - Page 1 of 13

