|  |  | Office of Facilities Planning and Engineering 7000 Fannin St., Suite 830 Houston, Texas 77030 www.uth.edu |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 22 05 13

PLUMBING MOTORS

This Standard Specification Section is controlled by the Office of Facilities Planning and Construction, UT System.  It is to be used as guideline on all UT System projects, unless deviations are approved in writing by the Project Manager.  It is not to be used for bidding, permitting, construction or any other purpose.  This document is the property of UT System, and use of this document, in part or in whole, for any purpose other than for a UT System project may not be done without written permission of UT System.

To receive current updates of standard specification Sections, please go to the web site at: http://www.utsystem.edu/fpc or contact the Office of Facilities Planning and Construction by phone at (512) 499-4600 or by fax at (512) 499-4604.

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 1 | June 2017 | 8 | New Specification section |

The University of Texas at Arlington · The University of Texas at Austin · The University of Texas at Dallas · The University of Texas at El Paso

The University of Texas of the Permian Basin · The University of Texas Rio Grande Valley · The University of Texas at San Antonio

The University of Texas at Tyler · The University of Texas Southwestern Medical Center · The University of Texas Medical Branch at Galveston

The University of Texas Health Science Center at Houston · The University of Texas Health Science Center at San Antonio

The University of Texas MD Anderson Cancer Center · The University of Texas Health Science Center at Tyler

SECTION 22 05 13 – plumbing motors

GENERAL

The following sections are to be included as if written herein:

Section 22 00 00 – Basic Plumbing Requirements

Section 22 05 29 – Plumbing Supports and Sleeves

Section 22 05 53 – Plumbing Identification

SECTION INCLUDES

Single phase electric motors

Three phase electric motors

The Contractor shall provide all motors required for equipment supplied under this Division of the work

RELATED WORK

Section 22 11 23 - Plumbing Equipment

Section 22 13 16.A - Plumbing Specialties

Section 22 63 13 - Medical Gas Systems

REFERENCES

AFBMA 9 - Load Ratings and Fatigue Life for Ball Bearings

AFBMA 11 - Load Ratings and Fatigue Life for Roller Bearings

ANSI/IEEE 112 - Test Procedure for Polyphase Induction Motors and Generators

ANSI/NEMA MG 1 - Motors and Generators

ANSI/NFPA 70 - National Electrical Code

SUBMITTALS

Submit product data under provisions of Section 22 00 00

Submit test results verifying nominal efficiency and power factor for motors 1 horsepower and larger.

Submit manufacturer's installation instructions under provisions of Section 22 00 00

OPERATION AND MAINTENANCE DATA

Submit operation and maintenance data under provisions of Section 22 00 00

Include assembly drawings, bearing data including replacement sizes, and lubrication instructions.

QUALIFICATIONS

Manufacturer:  Company specializing in manufacture of electric motors for commercial use, and their accessories, with minimum three years documented product development, testing, and manufacturing experience.

REGULATORY REQUIREMENTS

Conform to ANSI/NFPA 70.

DELIVERY, STORAGE, AND HANDLING

Deliver products to site under provisions of Section 22 00 00.

Store and protect products under provisions of Section 22 00 00.

Protect motors stored on site from weather and moisture by maintaining factory covers and suitable weather-proof covering.  For extended outdoor storage, remove motors from equipment and store separately.

WARRANTY

Provide five year manufacturer's warranty under provisions of Section 22 00 00.

Warranty:  Include coverage for motors 1 horsepower and larger.

PRODUCTS

GENERAL CONSTRUCTION AND REQUIREMENTS

All materials shall meet or exceed all applicable referenced standards, federal, state and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

Electrical Service:  Refer to Drawing schedules for required electrical characteristics.

Design for continuous operation in 40 degrees C environment and for temperature rise in accordance with ANSI/NEMA MG 1 limits for insulation class, Service Factor and motor enclosure type.

Open Drip-proof Motors:  Design for a service factor of 1.15 and a 90 degrees C temperature measured above 40 degrees C room ambient .

Totally Enclosed Motors:  Design for a service factor of 1.00 and an 80 degrees C maximum temperature rise in the same conditions.

Visible Stainless Steel Nameplate:  Indicating motor horsepower, voltage, phase, cycles, RPM, full load amps, locked rotor amps, frame size, manufacturer’s name and model number, Service Factor, Power Factor, efficiency.

Electrical Connection: Conduit connection boxes, threaded for conduit. For fractional horsepower motors where connection is made directly, provide threaded conduit connection in end frame. Provide adequately sized metal electrical connection box for conduit connection.

Motors shall be built in accordance with the latest ANSI, IEEE and NEMA Standards and shall be fully coordinated with the equipment served, shall be of sizes and electrical characteristics scheduled and of approved manufacturer as listed below or of the same manufacturer as the equipment which they serve.  Nameplate rating of motors shall match the characteristics scheduled.

All motors shall be designed for normal starting torque unless the driven machine requires high starting torque and shall be selected for quiet operation, free from magnetic hum.

All motors shall be provided with adequately sized electrical connection box with threaded hub for attachment of flexible conduit, unless bus duct connection is indicated. Where motors are connected to driven equipment by the use of a V-belt drive, they shall be furnished with adjustable rails.

Dynamic Balance shall be no greater than the vibration limits of the driven equipment as defined in the specifications.

All motors shall be provided with all copper windings, terminal wiring, and copper or bronze lugs.  AL/CU rated connectors are not allowed.

SINGLE PHASE POWER - SPLIT PHASE MOTORS

Starting Torque:  Less than 150 percent of full load torque.

Starting Current:  Up to seven times full load current.

Breakdown Torque:  Approximately 200 percent of full load torque.

Drip-proof Enclosure:  Class A (50 degrees C temperature rise) insulation, NEMA Service Factor, pre-lubricated sleeve or ball bearings.

Enclosed Motors:  Class A (50 degrees C temperature rise) insulation, 1.0 Service Factor, pre-lubricated ball bearings.

Single phase motors, in general, shall be less than 3/4 horsepower and shall be permanent split phase, capacitor start, induction run, 120 volt, 60 hertz motors with drip-proof enclosures except as hereinafter specified.  These motors shall have built-in thermal overload protection with automatic reset, and shall be rated for temperature rise as hereinbefore specified for 3-phase motors.

SINGLE PHASE POWER - PERMANENT-SPLIT CAPACITOR

Starting Torque:  Exceeding one fourth of full load torque.

Starting Current:  Up to six times full load current.

Multiple Speed:  Through tapped windings.

Open Drip-proof or Enclosed Air Over Enclosure:  Class A (50 degrees C temperature rise) insulation, minimum 1.0 Service Factor, pre-lubricated sleeve or ball bearings, automatic reset overload protector.

Single phase motors, in general, shall be less than 3/4 horsepower and shall be permanent split phase, capacitor start, induction run, 120 volt, 60 hertz motors.  These motors shall have built-in thermal overload protection with automatic reset, and shall be rated for temperature rise as hereinbefore specified for 3-phase motors.

SINGLE PHASE POWER - CAPACITOR START MOTORS

Starting Torque:  Three times full load torque.

Starting Current:  Less than five times full load current.

Pull-up Torque:  Up to 350 percent of full load torque.

Breakdown Torque:  Approximately 250 percent of full load torque.

Motors:  Capacitor in series with starting winding; capacitor-start/capacitor-run motors shall have two capacitors in parallel with run capacitor remaining in circuit at operating speeds.

Enclosures shall be of the open drip-proof type with a service factor of 1.15 and Class B insulation rated at 90 degrees C temperature rise measured above 40 degrees C room ambient condition at full load, unless otherwise noted.

Enclosed Motors:  Class A (50 degrees C temperature rise) insulation, 1.0 Service Factor, pre-lubricated ball bearings.

Single phase motors, in general, shall be less than 3/4 horsepower and shall be permanent split phase, capacitor start, induction run, 120 volt, 60 hertz motors.  These motors shall have built-in thermal overload protection with automatic reset, and shall be rated for temperature rise as hereinbefore specified for 3-phase motors.

THREE PHASE POWER - SQUIRREL CAGE MOTORS

Enclosures shall be of the open drip-proof type with a service factor of 1.15 (motor shall not run in Service Factor under normal operating conditions), and Class B insulation rated at 90 degrees C temperature rise measured above 40 degrees C room ambient condition at full load, unless otherwise noted.

In general, all motors 3/4 horsepower and larger, unless smaller motors are indicated to be supplied as 3-phase, shall be 3-phase and shall be squirrel cage high efficiency induction type with standard NEMA frame sizes.

Motors 1 HP and larger shall have integral frames.

Starting Torque:  Between one and one and one-half times full load torque.

Starting Current:  Six times full load current.

Power Output, Locked Rotor Torque, Breakdown or Pullout Torque:  NEMA Design B Characteristics.

Design, Construction, Testing, and Performance:  Conform to ANSI/NEMA MG 1 for Design B motors.

Insulation System:  NEMA Class B or better.

Testing Procedure:  In accordance with ANSI/IEEE 112, Test Method B.  Load test motors to determine freedom from electrical or mechanical defects and compliance with performance data.  Test and balance motors to limits defined in 2.01J.

Motor Frames:  NEMA standard T-frames of steel, aluminum, or cast iron with end brackets of cast iron or aluminum with steel inserts.

Thermistor System (Motor Frame Sizes 254T and Larger):   Three PTC thermistors imbedded in motor windings and epoxy encapsulated solid state control relay for wiring into motor starter; refer to Division 26. Bearings:  Ball or roller type, double shielded with continuous grease relief to accommodate excessive pressure caused by thermal expansion or over lubrication.  All motor bearings shall be factory pre-packed with a non-detergent lubricant, and shall be provided with lubrication fitting arranged to provide easy access when installed on the driven apparatus except as noted hereinafter.  Permanently lubricated factory-sealed motors may be provided in fractional HP sizes only where they are an integral part of a piece of approved apparatus.  All bearings shall be designed for L-10, 200,000 hour minimum life hours of continuous service.  Calculate bearing load with NEMA minimum V- belt pulley with belt center line at end of NEMA standard shaft extension.  Stamp bearing sizes on nameplate.

Sound Power Levels:  Refer to ANSI/NEMA MG 1.

Part Winding Start [Where Indicated:] [Above 254T Frame Size:]  Use part of winding to reduce locked rotor starting current to approximately 60 percent of full winding locked rotor current while providing approximately 50 percent of full winding locked rotor torque.

Weatherproof Epoxy [Sealed] [Treated] Motors (Where Indicated):  Epoxy [seal windings using vacuum and pressure] [coat windings] with rotor and starter surfaces protected with epoxy enamel.  Bearings shall be double shielded with waterproof non-washing grease.

Nominal Efficiency:  Meet or exceed values per 22 05 13-3.03 at full load and rated voltage when tested in accordance with ANSI/IEEE 112.

Nominal Power Service Factor:  Meet or exceed values per 22 05 13-3.02 at full load and rated voltage when tested in accordance with ANSI/IEEE 112.

Motors 1 HP and larger shall be provided with a copper frame grounding lug of hydraulic compression design, for installation by the electrical subcontractor.

Motors 3/4 HP and larger shall have 120V space heater that is energized only when motor is idle.  (Galveston only.)

Motors 10hp and larger shall be inverter duty rated and shall be provided with shaft grounding device.

STARTING EQUIPMENT:

Each motor shall be provided with proper starting equipment.  This equipment, unless hereinafter specified or scheduled to the contrary, shall be provided by the trade furnishing the motor.  All motor starting equipment provided by any one trade shall be of the same manufacture unless such starting equipment is an integral part of the equipment on which the motor is mounted.  The Plumbing Subcontractor shall furnish all starters for Division 22 work, except those starters scheduled to be provided in Division 26.

Motor starters shall conform to NEMA Standards for Industrial Control, #IC-1, latest issue, and shall be housed in NEMA Standard enclosures.  Control voltage in each starter shall be not more than 120 volts to ground, with an individual control transformer provided in each starter as required.  Manual starters for fractional horsepower single-phase motors shall be on-off or snap switch type combined with thermal overload device.  The switch shall be so constructed so that it cannot be held closed under a sustained motor overload.

Magnetic starters shall have thermal overload protection in each of the ungrounded legs and shall be solenoid operated.  Provide the correct size heater element to protect the motor and allow it to operate based on motor nameplate amperes and ambient temperatures anticipated for each individual motor.  Each starter shall be provided with a control power transformer or 120v control power circuit.

Pushbuttons with or without pilot lights, hand-off-automatic switches and other scheduled apparatus shall be standard duty type mounted in NEMA enclosures or in cover of starter as specified or scheduled, and shall  be furnished by the trade furnishing the starter except as specifically indicated elsewhere.

Hand-Off-Automatic switches for equipment which could damage itself if left in the "hand" position (such as sump pumps), shall be spring return to "off" from the "hand" position.

EXECUTION

APPLICATION

Motors drawing less than 250 Watts and intended for intermittent service may be germane to equipment manufacturer and need not conform to these specifications.

Motors shall be open drip-proof type, except where specifically noted otherwise.

Motors shall be energy efficient type.

Single phase motors for [shaft mounted fans] [oil burners] [centrifugal pumps] shall be split phase type.

Single phase motors for shaft mounted fans or blowers shall be permanent split capacitor type.

Single phase motors for [fans] [pumps] [blowers] [air compressors] shall be capacitor start type.

Single phase motors for [fans] [blowers] [pumps] shall be capacitor start, capacitor run type.

Motors located in [exterior locations] [wet air streams downstream of sprayed coil dehumidifiers] [draw thru cooling towers] [air-cooled condensers] [humidifiers] [direct drive axial fans] [roll filters] [explosion proof environments] [dust collection systems] [_______________] shall be totally enclosed type.

Motors located in [exterior locations] [wet air streams downstream of sprayed coil dehumidifiers] [draw thru cooling towers] [humidifiers] [_______________] shall be totally enclosed weatherproof epoxy-treated type.

Motors located in [exterior locations] [draw thru cooling towers] [_______________________] shall be totally enclosed weatherproof epoxy-sealed type.

NEMA OPEN MOTOR SERVICE FACTORS

| HP | 3600 RPM | 1800 RPM | 1200 RPM | 900 RPM |
| --- | --- | --- | --- | --- |
| 1/6-1/3 | 1.35 | 1.35 | 1.35 | 1.35 |
| 1/2 | 1.25 | 1.25 | 1.25 | 1.15 |
| 3/4 | 1.25 | 1.25 | 1.15 | 1.15 |
| 1 | 1.25 | 1.15 | 1.15 | 1.15 |
| 1.5-150 | 1.15 | 1.15 | 1.15 | 1.15 |

Motor Efficiencies* – Nominal, full load, three phase

| - Minimum Nominal Full Load Efficiency (5) for Motors Manufactured on or after December 19, 2010 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - Open Drip-Proof Motors |  |  |  |  | - Totally Enclosed Fan Cooled Motors |  |  |  |
| - Number of Poles | - 2 | - 4 | - 6 | - 8 | - 2 | - 4 | - 6 | - 8 |
| - Synchronous Speed (RPM) | - 3600 | - 1800 | - 1200 | - 900 | - 3600 | - 1800 | - 1200 | - 900 |
| - Motor Horsepower |  |  |  |  |  |  |  |  |
| - 1 | - NR | - 82.5 | - 80.0 | - 74.0 | - 75.5 | - 82.5 | - 80.0 | - 74.0 |
| - 1.5 | - 82.5 | - 84.0 | - 84.0 | - 75.5 | - 82.5 | - 84.0 | - 85.5 | - 77.0 |
| - 2 | - 84.0 | - 84.0 | - 85.5 | - 85.5 | - 84.0 | - 84.0 | - 86.5 | - 82.5 |
| - 3 | - 84.0 | - 86.5 | - 86.5 | - 86.5 | - 85.5 | - 87.5 | - 87.5 | - 84.0 |
| - 5 | - 85.5 | - 87.5 | - 87.5 | - 87.5 | - 87.5 | - 87.5 | - 87.5 | - 85.5 |
| - 7.5 | - 87.5 | - 88.5 | - 88.5 | - 88.5 | - 88.5 | - 89.5 | - 89.5 | - 85.5 |
| - 10 | - 88.5 | - 89.5 | - 90.2 | - 89.5 | - 89.5 | - 89.5 | - 89.5 | - 88.5 |
| - 15 | - 89.5 | - 91.0 | - 90.2 | - 89.5 | - 90.2 | - 91.0 | - 90.2 | - 88.5 |
| - 20 | - 90.2 | - 91.0 | - 91.0 | - 90.2 | - 90.2 | - 91.0 | - 90.2 | - 89.5 |
| - 25 | - 91.0 | - 91.7 | - 91.7 | - 90.2 | - 91.0 | - 92.4 | - 91.7 | - 89.5 |
| - 30 | - 91.0 | - 92.4 | - 92.4 | - 91.0 | - 91.0 | - 92.4 | - 91.7 | - 91.0 |
| - 40 | - 91.7 | - 93.0 | - 93.0 | - 91.0 | - 91.7 | - 93.0 | - 93.0 | - 93.0 |
| - 50 | - 92.4 | - 93.0 | - 93.0 | - 91.7 | - 92.4 | - 93.0 | - 93.0 | - 91.7 |
| - 60 | - 93.0 | - 93.6 | - 93.6 | - 92.4 | - 93.0 | - 93.6 | - 93.6 | - 91.7 |
| - 75 | - 93.0 | - 94.1 | - 93.6 | - 93.6 | - 93.0 | - 94.1 | - 93.6 | - 93.0 |
| - 100 | - 93.0 | - 94.1 | - 94.1 | - 93.6 | - 93.6 | - 94.5 | - 94.1 | - 93.0 |
| - 125 | - 93.6 | - 94.5 | - 94.1 | - 93.6 | - 94.5 | - 94.5 | - 94.1 | - 93.6 |
| - 150 | - 93.6 | - 95.0 | - 94.5 | - 93.6 | - 94.5 | - 95.0 | - 95.0 | - 93.6 |
| - 200 | - 94.5 | - 95.0 | - 94.5 | - 93.6 | - 95.0 | - 95.0 | - 95.0 | - 94.1 |
| - 250 | - 94.5 | - 95.4 | - 95.4 | - 94.5 | - 95.4 | - 95.0 | - 95.0 | - 94.5 |
| - 300 | - 95.0 | - 95.4 | - 95.4 | - NR | - 95.4 | - 95.4 | - 95.0 | - NR |
| - 350 | - 95.0 | - 95.4 | - 95.4 | - NR | - 95.4 | - 95.4 | - 95.0 | - NR |
| - 400 | - 95.4 | - 95.4 | - NR | - NR | - 95.4 | - 95.4 | - NR | - NR |
| - 450 | - 95.8 | - 95.8 | - NR | - NR | - 95.4 | - 95.4 | - NR | - NR |
| - 500 | - 95.8 | - 95.8 | - NR | - NR | - 95.4 | - 95.8 | - NR | - NR |

- RE: ANSI/ASHRAE/IES Standard 90.1-ZD10, Table 10.8c minimum nominal full-load efficiency of general purpose electric motors (subtype 11 and design 13)

*Reference NEMA MG 1-2006 Table 12-12.

END OF SECTION 22 05 13