|  |  | Office of Facilities Planning and Engineering 7000 Fannin St., Suite 830 Houston, Texas 77030 www.uth.edu |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 22 07 19

PLUMBING INSULATION

This Standard Specification Section is controlled by the Office of Facilities Planning and Construction, UT System.  It is to be used as guideline on all UT System projects, unless deviations are approved in writing by the Project Manager.  It is not to be used for bidding, permitting, construction or any other purpose.  This document is the property of UT System, and use of this document, in part or in whole, for any purpose other than for a UT System project may not be done without written permission of UT System.

To receive current updates of standard specification Sections, please go to the web site at: http://www.utsystem.edu/fpc or contact the Office of Facilities Planning and Construction by phone at (512) 499-4600 or by fax at (512) 499-4604.

The issuance and revision history of this Section is tabulated below.  Please destroy any previous copy in your possession

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 1 | June 2017 | 8 | Specification update |

The University of Texas at Arlington · The University of Texas at Austin · The University of Texas at Dallas · The University of Texas at El Paso

The University of Texas of the Permian Basin · The University of Texas Rio Grande Valley · The University of Texas at San Antonio

The University of Texas at Tyler · The University of Texas Southwestern Medical Center · The University of Texas Medical Branch at Galveston

The University of Texas Health Science Center at Houston · The University of Texas Health Science Center at San Antonio

The University of Texas MD Anderson Cancer Center · The University of Texas Health Science Center at Tyler

SECTION 22 07 19 – PLUMBING INSULATION

GENERAL

  - The following sections are to be included as if written herein:

22 00 00 -- Basic Plumbing Requirements

22 05 29 – Plumbing Supports and Sleeves

22 05 53 – Plumbing Identification

  - SECTION INCLUDES

    - Piping insulation

Jackets and accessories

  - PRODUCTS FURNISHED BUT NOT INSTALLED UNDER THIS SECTION

    - Section 22 13 16- Plumbing Piping:  Placement of hangers and hanger inserts.

  - RELATED SECTIONS

    - Division 9 - Painting

  - REFERENCES

    - ASTM B209   Aluminum and Aluminum Alloy Sheet and Plate.

ASTM C177   Steady State Heat Flux Measurements and Thermal Transmission Properties by Means of the Guarded  Hot Plate Apparatus.

ASTM C195   Mineral Fiber Thermal Insulation Cement.

ASTM C335   Steady State Heat Transfer Properties of Horizontal Pipe Insulation.

ASTM C449   Mineral Fiber Hydraulic setting Thermal

ASTM C518   Steady State Heat Flux Measurements and Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus.

ASTM C533   Calcium Silicate Block and Pipe Thermal Insulation.

ASTM C534   Preformed Flexible Elastomeric Cellular Thermal Insulation in Sheet and Tubular Form.

ASTM C547   Mineral Fiber Preformed Pipe Insulation.

ASTM C552   Cellular Glass Block and Pipe Thermal Insulation.

ASTM C578   Preformed, Block Type Cellular Polystyrene Thermal Insulation.

ASTM C585   Inner and Outer Diameters of Rigid Thermal Insulation for Nominal Sizes of Pipe and Tubing (NPS System).

ASTM C921   Properties of Jacketing Materials for Thermal Insulation.

ASTM D1056   Flexible Cellular Materials   Sponge or Expanded Rubber.

ASTM D2842   Water Absorption of Rigid Cellular Plastics.

ASTM E84   Surface Burning Characteristics of Building Materials.

ASTM E96   Water Vapor Transmission of Materials.

NFPA 255   Surface Burning Characteristics of Building Materials.

UL 723   Surface Burning Characteristics of Building Materials.

ASHRAE 90.1 – Energy Standard for Buildings Except Low Rise Residential Buildings

  - SUBMITTALS

    - Submit under provisions of Section 22 00 00.

Product Data:  Provide product description, list of materials ‘k’ value, ‘R’ value, mean temperature rating, and thickness for each service, and locations.

Samples:  When requested, submit two samples of any representative size illustrating each insulation type.

Manufacturer’s Installation Instructions:  Indicate procedures which ensure acceptable workmanship and installation standards will be achieved.

  - QUALITY ASSURANCE

    - All insulation, jacket, adhesives, mastics, sealers, etc., utilized in the fabrication of these systems shall meet NFPA for fire resistant ratings (maximum of 25 flame spread and 50 smoke developed ratings) and shall be approved by the insulation manufacturer for guaranteed performances when incorporated into their insulation system, unless a specific product is specified for a specific application, and is stated as an exception to this requirement.  Certificates to this effect shall be submitted along with Contractor’s submittal data for this section of the Specifications.  No material may be used that, when tested by the ASTM E84 89 test method, is found to melt, drip or delaminate to such a degree that the continuity of the flame front is destroyed, thereby resulting in an artificially low flame spread rating.

All surfaces to be insulated shall be clean and dry before applying the insulation.  All sections of molded pipe covering shall be firmly butted together.  Where an insulation covering is applied, it shall lap the adjoining section of insulation by at least three inches (3”).  Where insulation terminates, it shall be neatly beveled and finished.  No insulation shall be applied until the pipe, duct, etc., have been pressure tested and found tight.  Piping, flexible connections, flanges, valves, strainers, and unions shall be covered unless specifically noted otherwise.  Flexible connections on duct shall not be covered.  All materials used shall be fire retardant or nonflammable.  Refer to Section 22 00 00.

All piping shall be insulated as indicated on the Drawings, as specified herein, and as required for a complete system.  In each case, the insulation shall be equal to that specified and materials applied and finished as described in these Specifications.

To be considered, alternate materials shall have equivalent thermal and moisture resistance of the specified materials.

  - QUALIFICATIONS

    - All insulation shall be applied by mechanics skilled in this particular work and regularly engaged in such occupation.

All insulation shall be applied in strict accordance with these Specifications and with factory printed recommendations on items not herein mentioned.  Unsightly, inadequate, or sloppy work will not be acceptable, and all such work shall be removed and replaced as many times as necessary to achieve an acceptable installation. The company performing the work of this section shall have a minimum of three years’ experience specializing in the trade.

  - DELIVERY, STORAGE, AND HANDLING

    - Deliver, store, protect, and handle products to site under provisions of Section 22 00 00.

Deliver materials to site in original factory packaging, labeled with manufacturer’s identification, including product thermal ratings and thickness.

Store insulation in original wrapping and protect from weather and construction traffic. Protect insulation against dirt, water, chemical, and mechanical damage.

  - ENVIRONMENTAL REQUIREMENTS

    - Maintain ambient temperatures and conditions required by manufacturers of adhesives, mastics, and insulation cements.

Maintain temperature during and after installation for minimum period of 24 hours.

All insulation materials to be asbestos free.

PRODUCTS

  - DOMESTIC HOT AND COLD WATER

All domestic hot and cold water lines in buildings, including valves, strainers, unions, flanges, etc., except where specifically noted to the contrary, shall be insulated.

All domestic cold water lines shall be insulated as scheduled with preformed fiberglass insulation with a factory applied All Service Jacket, vapor sealing all joints, and factory performed fittings with vapor seal, or a flexible, “25-50” rated, closed cell elastomeric thermal insulation such as “Self Seal Armaflex 2000”.  Elastomeric products shall be supplied in a pre-slit tubular form with a pressure sensitive adhesive system for closure and vapor sealing of the longitudinal joint.  All elastomeric insulating products shall be guaranteed not to react with copper piping.  Valves shall be insulated with mitered pipe covering with voids filled with glass fiber blanket insulation.  Valves and fittings shall be vapor sealed with a water base asphaltic emulsion.  Fittings on concealed insulation shall be built up to the thickness of adjacent insulation with glass fiber fitting wrap and shall be finished with Glasfab tape embedded in vapor barrier emulsion.  Exposed fitting insulation shall be built up to same thickness as adjoining pipe insulation with one coat cement and after drying shall be finished with a white vapor seal and canvas jacket secured with “Arabol” adhesive and be suitable for painting.  Seams in jacket shall be placed in the least noticeable locations.  Where seams, joint or fittings are rough they shall be covered with an application of insulating cement troweled on smoothly before the canvas is applied with Arabol adhesive.  The canvas must be free of wrinkles and have a smooth, neat appearance.

All domestic hot water piping systems shall be insulated as specified above for cold water except the vapor barrier may be deleted and the lap and butt joints secured with staples and a field applied adhesive (self sealing lap and butt joints alone are not acceptable).  The insulation thickness shall be as scheduled. Where service temperature exceeds 250F, insulation shall contain high temp binders.

The only domestic hot and cold water piping that will not require insulation is the exposed runouts under non-handicap plumbing fixtures.  Where pipe chases are tight, adequate provision shall be made at the rough in stage utilizing offset fittings or other means (except springing the pipe) to insure that insulation can be applied throughout the length of the pipe.

  - ROOF DRAIN AND OVERFLOW DRAIN PIPING

    - All horizontal runs of roof drain piping in the building, and the bottom of all roof drains shall be insulated and sealed to the roof. Insulation shall be as specified for domestic cold water.  Vertical roof drain piping inside the building shall not be insulated.

  - CONDENSATE DRAINAGE AND WATER RECOVERY.

    - All piping receiving condensate drainage and water recovery shall be insulated, as specified herein.

  - type A:  fiberglass

    - Owens Corning or equal glass fiber insulation piping insulation with a “K” factor of 0.23 BTU-In/Hr.-degree F at 75°F and 0.32 BTU-In/Hr.-degree F at 250°

Rated maximum service temperature of 850°F.

Maximum density of 3.5-5.5 lbs/ft³

Compressive strength of 28.5 psi minimum when tested in accordance with ASTM C165.

Rated as 25 flame spread and 50 smoke developed when tested in accordance with ASTM E84, UL 723, CAN/ULC-S102-M88 or NFPA 255.

Certified to meet the requirements of ASTM C795 for use over stainless steel.

Rated as noncombustible when tested in accordance with ASTM E136.

Insulation treated with water resistant resin on the surface and within each layer of the insulation

  - type B: closed cell elastomeric

    - Closed cell elastomeric piping insulation with a “K” factor of 0.25 BTU-In/Hr.-degree F at as manufactured by Armacell or equal.

Rated maximum service temperature of 220°F.

Rated as 25 flame spread and 50 smoke developed when tested in accordance with ASTM E84, UL 723, CAN/ULC-S102-M88 or NFPA 255.

Certified to meet the requirements of ASTM C795 for use over stainless steel.

Rated as noncombustible when tested in accordance with ASTM E136.

  - PROTECTIVE JACKETING

    - Aluminum Jacketing and fitting covers:0.016 aluminum smooth as manufactured by Premetco or Childers.  The jacket shall be pre-cut, pre-rolled, and lapped a minimum of two inches (2”) In all directions to shed water.  The metal shall be secured at each joint with a minimum of one each (1 ea.) ¾” wide .020 aluminum or stainless steel band and seal. The metal jacketing and fitting covers shall be fabricated of 0.016” aluminum or stainless steel with a smooth finish.

PVC Jacketing:  Proto Corp. LoSmoke PVC jacketing and fitting covers Material shall have 25/50 rating and shall be limited to piping systems operating at 140 degrees or below.

INSTALLATION

  - EXAMINATION

Verify that piping has been tested before applying insulation materials.

Verify that surfaces are clean, foreign material removed, and dry.

  - INSTALLATION

    - Install materials in accordance with manufacturer’s instructions in the absence of specific instruction herein.

On exposed piping, locate insulation and cover seams in least visible locations, but not higher than at the side of the pipe at the “90°” position, with the seam lapped such that the lap is directed down.

Continue insulation through walls, sleeves, pipe hangers, and other pipe penetrations.

For insulated pipes conveying fluids above ambient temperature:

Provide standard jackets, with or without vapor barrier, factory applied or field applied.

Insulate fittings, joints, and valves with insulation of like material and thickness as adjoining pipe.

For hot piping conveying fluids 140 degrees F or less, do not insulate flanges and unions at equipment, but bevel and seal ends of insulation.

For piping systems being heat traced, provide insulation one pipe size larger to accommodate the heat tracing cable.

  - INSERTS, SUPPORTS and SHIELDS

    - Application:  Piping 3/4 inch diameter or larger for all systems.

Shields:  Install between pipe hangers or pipe hanger rolls and inserts. Hangers shall be on the outside of the insulation and shall not be in contact with the pipe.  Curved metal shields shall be used between the hangers or support points and the bottom of the insulated pipe for insulated pipes 3/4” and larger.  Curved metal shields shall be designed to limit the bearing stress on the insulation to 35 psi and shall be curved to fit up to mid-perimeter of the insulated pipe. Shields shall be made of galvanized iron, or black iron painted on both sides with two coats of aluminum paint. Required metal shield sizes are as follows:

| Nominal IPS | Metal Thickness of Shield | Lengths |
| --- | --- | --- |
| up thru 2” | 14 gauge | 12” |
| thru 6” | 12 gauge | 16” |
| and above | 10 gauge | 20” |

Insert Location:  Between support shield and piping and under the finish jacket.

Insert Configuration:  Minimum 2” inches longer than length of shield, of same thickness and contour as adjoining insulation; may be factory fabricated.

Insert Material:  Heavy density insulating material suitable for the planned temperature range, and the weight of the pipe.

The shields at support points shall be secured with ½” x 0.016” stainless steel bands and seals.

Finish insulation at supports, protrusions, and interruptions.

In lieu of the above the following system of support may be used:

At the pipe support positions, the insulation and vapor barrier shall be continuous and shall not be punctured by the support. The insulation at the support shall be the full circumference of 5lbs/ft3 INSUL-PHEN Foam material to withstand the bearing loads transmitted from the pipe to the support, it shall extend for at least 1" on either side of the support to allow sealing of the joints with the pipe insulation jacket.

The load bearing insulation at the support shall be capable of withstanding the maximum static compressive loads generated by pipe supported at the centers shown in Table Variations: Pipe loads greater than those generated at the support centers shown in Table 1 shall be referred to the manufacturer to establish the length and density of the insulated support block. The support centers are based on the weight of Sch 80 pipe filled with water and covered with 1" thickness of 2.2 lbs/ft3 standard insulation including FSK/ASJ vapor barrier.

Table 1 K Block Support Centers

| Nominal Pipe Size | 3/4 | 1 | 1 1/4 | 2 | 2 1/2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Max support centers (feet) Sch 80 pipe filled with water covered with 1" of Standard Insulation | 6.5 | 6.5 | 6.5 | 10 | 10 | 10 | 10 | 10 | 14 | 14 | 14 | 20 | 20 | 20 | 20 | 20 |
| Metal Saddle Gauge (Galvanized Steel) | 22 | 22 | 22 | 20 | 20 | 20 | 16 | 14 | 14 | 14 | 14 | 14 | 114 | 14 | 14 | 14 |
| Length of K Block (inches) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 12 | 12 |

The Insulation at supports shall be a Kooltherm K Block.  K Blocks shall be faced with factory applied FSK/ASJ vapor barrier and fitted with a galvanized steel 1800 saddle bonded to the bottom section of the K Block, for all pipe sizes 1 1/2"  and larger.

The vapor barrier shall be completed by the use of a FSK/ASJ overlap and factory applied self-seal lap tape and sealed with vapor barrier adhesive.

At all support positions, other than those where the insulated pipe support block is surrounded by a clip or saddle in direct contact with the block, a block designed to accept the loads generated by the pipe shall be presented to the engineer for approval. e.g. Of the type Kooltherm products K Block. Ref:-Kooltherm sketch 106/2c for use with Roller or flat beam support.

In all cases where roller supports are used the length of the insulation and the wearing plate where fitted shall extend beyond the limits of the pipe movement.

For purpose of definition in this Specification: “concealed” areas are those areas which cannot be seen by the building occupants, and “exposed” areas are all areas which are exposed to view by the building occupants, including under counter and inside cabinet areas, plus all mechanical rooms.

Self-Sealing Lap and butt joints will not be acceptable as the only seal on piping insulation joints.  Self Sealing Lap and butt joints may be utilized only if the joints are additionally secured with field applied vapor barrier adhesive (on piping Systems requiring vapor barriers) or staples and field applied adhesive (on piping system which do not require a vapor barrier jacket).  Mechanical fasteners shall be used whenever possible to assure permanent installation.

Insulation minimum thickness shall be as scheduled; however, additional thickness shall be provided to prevent condensation on the cold surfaces and to provide a maximum exterior insulation surface of 140 degrees F on the hot surfaces.

All insulated piping in the mechanical rooms within 8’-0” of the floor shall be encased in an aluminum protective jacket, and where applicable, finish at top with nickel-plated brass flange plate with set screws or end joint sealing butt strips.

All piping with crawl space, outside building and in tunnels shall be protected with an aluminum jacket.

  - PAINTING

    - All exposed insulation shall be prepared to receive painting specified under Section 09 91 00.

  - insulation application schedule

Where minimum scheduled thickness exceeds the thickness required to meet the minimum R-Value, provide the minimum scheduled thickness.

| Service | Pipe Diameter Inches | Location | Fluid Temp Degrees F | Min. R-Value | Insulation Type and Thickness in Inches |  |
| --- | --- | --- | --- | --- | --- | --- |
| Domestic Cold Water and Makeup Water | All Sizes | Interior | Ambient | 4.2 | Type A 1 | Type B 1 |
| Domestic Cold Water and Domestic Hot Water | All Sizes | Interior, Serving Single Fixtures | Ambient | 2.1 | Type A 1/2 | Type B 1/2 |
| Domestic Hot Water Supply & Return | 1 to 1-1/4 | Interior | 105-140 | 4.2 | Type A 1 | Type B 1 |
| Domestic Hot Water Supply & Return | 1-1/2 and up | Interior | 105-140 | 6.4 | Type A 1-1/2 | Type B 1-1/2 |
| AHU Drains | All Sizes | Interior | Ambient | 4.2 | Type A 1 | Type B 1 |
| Drinking Fountain Drains | All Sizes | Interior | 40-55 | 4.2 | Type A 1 | Type B 1 |
| Floor Drain Bodies Receiving AHU Condensate Including P-Trap and a Minimum 20’ of Pipe | All Sizes | Interior | 40-55 | 4.2 | Type A 1 | Type B 1 |
| Floor Drain Bodies Receiving AHU Condensate Including P-Trap and a Minimum 20’ of Pipe | All Sizes | Tunnel, Outside, in Crawl Space | 40-55 | 2.9 | Type A 1 | Type B 1 |
| Roof Drain and Overflow Drain Bodies and horizontal Piping Extending to Vertical Downspout | All Sizes | Interior | Ambient | 4.2 | Type A 1 | Type B 1 |

All insulation R-Values shall be the greater of what is scheduled above or required to meet ASHRAE 90.1-2010.

Minimum ‘R’ does not consider water vapor transmission and condensation.  Additional insulation and/or vapor retarders may be required to limit water vapor transmission and condensation under extreme conditions.

A minus 15 percent tolerance, on the insulation performance listed shall be permitted for manufacturers' standard insulation systems.

In non-conditioned mechanical rooms and all crawl spaces, insulation shall prevent formation of surface condensation under conditions of 95°F, 95%RH, and zero wind speed.  Provide manufacturer’s certification of this performance on submittal data.

END OF SECTION 22 07 19