|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 777030 WWW.UTH.EDU |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 22 15 13

COMPRESSED AIR SYSTEM

This Standard Specification Section is controlled by the Office of Facilities Planning and Construction, UT System.  It is to be used as guideline on all UT System projects, unless deviations are approved in writing by the Project Manager.  It is not to be used for bidding, permitting, construction or any other purpose.  This document is the property of UT System, and use of this document, in part or in whole, for any purpose other than for a UT System project may not be done without written permission of UT System.

To receive current updates of standard specification Sections, please go to the web site at: http://www.utsystem.edu/fpc or contact the Office of Facilities Planning and Construction by phone at (512) 499-4600 or by fax at (512) 499-4604.

The issuance and revision history of this Section is tabulated below.  Please destroy any previous copy in your possession.

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | March 1998 | 7 | Original |
| 1 | May 2004 | 1 | Revised Cover Page |
| 2 | February 2007 | 7 | Format, 1.00 |
| 3 | June 2017 | 8 | Specification update |

The University of Texas at Arlington · The University of Texas at Austin · The University of Texas at Dallas · The University of Texas at El Paso

The University of Texas of the Permian Basin · The University of Texas Rio Grande Valley · The University of Texas at San Antonio

The University of Texas at Tyler · The University of Texas Southwestern Medical Center · The University of Texas Medical Branch at Galveston

The University of Texas Health Science Center at Houston · The University of Texas Health Science Center at San Antonio

The University of Texas MD Anderson Cancer Center · The University of Texas Health Science Center at Tyler

SECTION 22 15 13 - COMPRESSED AIR SYSTEM

- GENERAL

- THE FOLLOWING SECTIONS ARE TO BE INCLUDED AS IF WRITTEN HEREIN:

    - Section 22 00 00 – Basic Plumbing Requirements

    - Section 22 05 29 – Plumbing Supports and Sleeves

    - Section 22 05 53 – Plumbing Identification

- SECTION INCLUDES

- Pipe and Pipe Fittings

- Air Compressor

- Air Receiver and Accessories

- Aftercooler

- Air Dryer

- Pressure Reducing Station

- PRODUCTS INSTALLED BUT NOT FURNISHED UNDER THIS SECTION

- Section 01 11 00 - Summary of Work:  Owner furnished [air compressor] [air outlet fittings] [________].

- RELATED SECTIONS

- Section 03300 - Cast-in-Place Concrete

- Section 22 05 48 – Plumbing Vibration Isolation

- Section 22 13 16 - Plumbing Piping

- Section 26 05 19 - Insulated Conductors

- Section 26 27 26 - Wiring Devices

- REFERENCES

- ASME - Boiler and Pressure Vessel Code

- ASME B16.3 - Malleable Iron Threaded Fittings

- ASME B16.18 - Cast Bronze Solder-Joint Pressure Fittings

- ASME B16.22 - Wrought Copper and Bronze Solder-Joint Pressure Fittings

- ASME B16.26 - Cast Bronze Fittings for Flared Copper Tubes

- ASME B31.1 - Power Piping

- ASME B31.9 - Building Services Piping

- ASTM A53 - Pipe, Steel, Black and Hot-Dipped Zinc Coated, Welded and Seamless

- ASTM A120 - Pipe, Steel, Black and Hot-Dipped Zinc Coated (Galvanized), Welded and Seamless, for Ordinary Uses

- ASTM A234 - Pipe Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and Elevated Temperatures

- ASTM B32 - Solder Metal

- ASTM B88 - Seamless Copper Water Tube

- ASTM D2513 - Thermoplastic Gas Pressure Pipe, Tubing and Fittings

- ASTM D2683 - Socket-Type Polyethylene Fillings for Outside Diameter-Controlled Polyethylene Pipe

- NFPA 70 - National Electrical Code

- SUBMITTALS

- Submit under provisions of Section 22 00 00.

- Shop Drawings:  Indicate piping system schematic with electrical characteristics and connection requirements.

- Product Data:  Provide manufacturers catalog literature with capacity, weight, and electrical characteristics and connection requirements.

- Test Reports:  Submit inspector's certificate for air receiver for inclusion in Operating and Maintenance Manuals.

- Manufacturer's Installation Instructions:  Indicate hoisting and setting requirements, starting procedures.

- PROJECT RECORD DOCUMENTS

    - Submit under provisions of Section 22 00 00.

    - Record actual locations of equipment and components.  Modify shop drawings to indicate final locations.

- OPERATION AND MAINTENANCE DATA

- Submit under provisions of Section 22 00 00.

- Operation Data:  Submit for air compressor, air receiver and accessories, after cooler, air dryer, and pressure reducing station.

- Maintenance Data:  Submit for air compressor, air receiver and accessories, after cooler, air dryer, and pressure reducing station.

- REGULATORY REQUIREMENTS

- Conform to ASME codes for installation of pressure vessels.

- Provide certificate of compliance from Factory Mutual indicating approval of air receiver.

- Products Requiring Electrical Connection:  Listed and classified by Underwriters Laboratories, Inc., as suitable for the purpose specified and indicated.

- DELIVERY, STORAGE, AND HANDLING

- Deliver, store, protect and handle products to site under provisions of Section 22 00 00.

- Accept air compressors, air dryer on site in factory fabricated containers with shipping skids and plastic pipe end protectors in place.  Inspect for damage.

- Protect piping and equipment from weather and construction traffic.

- WARRANTY

- Provide five-year warranty under provisions of Section 22 00 00.

- Warranty:  Include coverage for air compressors, [___________].

- MAINTENANCE MATERIALS

- Provide maintenance materials under provisions of 22 00 00.

- [____] air compressor inlet filter elements.

- [___] air compressor outlet (supply) filter elements.

- [___] air dryer inlet filter elements.

- [___] air dryer discharge filter elements

- [___] purge mufflers for air dryers.

- PRODUCTS

      - COMPRESSOR MODULES:

- The compressors shall be continuous duty rated scroll types with sealed bearings.  The design shall be single stage, air-cooled, consisting of one fixed and one orbiting scroll sealed with PTFE tip seals between the scroll halves and rated for 120 psig discharge pressure.  The scrolls shall be protected from dust or contamination with a two part face seal.  Orbiting bearings shall be grease filled and permanently sealed type requiring no lubrication at any time.  The drive bearing shall be grease filled and lip sealed with a maintenance interval of not less than 10,000 hours.  The scroll case shall be constructed of die cast aluminum.  Maximum heat dissipation shall be achieved through an integral cooling fan and air ducting.  The compressors shall be v-belt driven and protected by an OSHA approved totally enclosed belt guard.  A sliding motor mounting base that is fully adjustable with one adjusting screw shall achieve belt tensioning.

- Each compressor module shall have a piped intake manifold with one inline inlet air filter with isolation valve and a high inlet vacuum switch.

- Each compressor module shall be equipped with an integral air-cooled aftercooler designed for a maximum approach temperature of 15°F complete with automatic solenoid drain valve.

- Each compressor shall be equipped with a wired high discharge air temperature shutdown switch.

- The compressor module discharge line shall include a flex connector, safety relief valve, isolation valve and check valve.  The discharge piping of each compressor module shall incorporate an integral valve to provide load-less starting and rapid air evacuation between the check valve and scroll discharge at shutdown to produce less than 1/4 revolution of reverse rotation of the scroll.

- Compressor motor shall be a NEMA rated, open drip-proof, 3600 RPM, with 1.15 service factor suitable for 460 volt, 60 hertz, 3 phase electrical service.

      - AIR RECEIVER

- The air receiver shall be corrosion resistant, National Board Certified, Comply with Section VIII, Unfired Pressure Vessels, of the ASME Boiler and Pressure Vessel Code, be ASME Code stamped, and rated for a minimum 150 PSIG design pressure.

- The air receiver shall be of a capacity sufficient to prevent the compressors from short-cycling.

- The receiver shall be provided with a pressure indicator, liquid level gauge sight glass, safety pressure relief valve, manual drain valve, and a timed automatic solenoid drain valve.

- Air receiver shall be provided with a three-valve bypass to permit service to the receiver without shutting down the air system.

      - CONTROL SYSTEM

- The control system shall be NEMA 12 enclosure and U.L. labeled, factory pre-mounted and pre-wired.

- The control system shall provide automatic lead/lag sequencing with circuit breaker disconnects for each motor with external operators, full voltage motor starters with overload protection, and 120V control circuit transformers for each motor circuit.

- The control system shall include local visual and audible reserve unit alarm with isolated contacts for remote alarm, hand-off-auto lighted selector switches and runtime hour meters.

- Automatic alternation of the compressors shall allow equal division of operating time with provisions for simultaneous operation and automatic activation of reserve unit.

- Additional lag compressors shall automatically activate when compressors in operation are incapable of maintaining the required pressure.

- Local visual and audible alarm indication for high discharge air temperature shutdown with isolated contacts for remote alarm shall be included.

- A pressure gauge shall be provided in the control panel.

- Complete with dry contacts and a 4-20 Ma signal for remote monitoring to the DDC system for compressor status (indicating operation of any compressor is on), and compressor failure alarm (alarm upon only compressor failure).

      - AIR DRYER

- Air dryers shall be duplex twin type tower absorption/regenerative desiccant type, individually sized for peak calculated demand and capable of producing a -40°F pressure dew point for lab air use.

- Fully automatic with a 0.01 micron cartridge type coalescing pre-filter and a 1 micron particulate cartridge type after-filter.

- Power on/off switch and light, ASME relief valve with factory installed gauges on inlet and discharge.

- Complete with factory installed alumina desiccant.

- Membrane condensate drain.

- ASME coded pressure vessel rated for 150 psi.

- NEMA 4 control panel with solid state controls and moisture indicator, dew point monitor and automatic on demand air purge saving control.

- Entire air dryer shall be totally factory pre-packaged and factory tested prior to shipment.

- Electrical requirements shall be 120 volt, single phase, 60 hertz.

- Complete with 4-20 Ma signal for remote monitoring to the DDC system for High Humidity Alarm.

      - FILTRATION/PRESSURE REGULATOR ASSEMBLY

- Consisting of (2) activated carbon filters with differential pressure gauge and change indicator.

- Dual inline pressure regulator assembly consisting of (2) pressure regulators with pressure gauges, inlet and outlet ball valves and pressure relief valve.

- Filters and regulators shall be arranged so that isolation of one filter or regulator will not affect the operation of the second filter or regulator.

- The pressure regulators shall be set to discharge [__] psig

      - PIPING:

- Compressed air piping shall be ASTM SpecificationB280 or B819, Type K, hard drawn, seamless copper tubing factory cleaned sealed marked for oxygen service with wrought copper solder fittings complying with ANSI B16.22.  All joints shall be brazed under a nitrogen purge.  Cast copper alloy fittings shall not be permitted.  No ferrous piping will be permitted in the system.  Where threaded nipples are required these shall be I.P.S. brass.

- All piping shall be pitched back so as to drain to the point shown on the Drawings.  All branch air take-offs shall be made from the top of the mains.

- All joining operations shall be done with pure dry nitrogen flowing through the pipe to prevent oxidation and scale information. During joining operations, nitrogen flow shall be verified by an oxygen sensor at the free end of the piping and by a pressure alarm on the nitrogen supply. When there are no active joining operations being performed, the system shall be securely sealed and maintained with a nitrogen charge in the sealed system. Brazed joints shall be made using a brazing alloy that exhibits a melting temperature in excess of 538° F. Copper-to-copper joints shall be brazed using a copper-phosphorus or copper-phosphorus-silver brazing filler metal (BCuP series) without flux. Flux shall only be used when brazing dissimilar metals such a copper and bronze or brass, using a silver (BAg sense) brazing filler metal. Brazing alloy shall comply with ANSI/AWS A5.8.F. Straight-threaded connections, including unions, flared and compression-type connections, including connections to station outlets and inlets, alarm devices, and other components shall not be permitted. Before erection, all pipe, tubing, valves and fittings (except those supplied expressly cleaned by manufacturer) shall be thoroughly cleansed of all grease, oil and other combustible materials by washing in a hot solution of sodium carbonate or trisodium phosphate mixed in equal proportions of one pound to three gallons of water.  Scrubbing and continuous agitation of the parts shall be employed where necessary to remove all deposits and to insure complete cleansing.  After washing, all materials shall be rinsed thoroughly in clean, hot water.  After rinsing, great care must be exercised in the storage and handling of all materials and in the condition of tools used in cutting and reaming to prevent oil or grease being introduced into the tubing.  Where such contamination is known to have occurred, the materials affected must be rewashed and then rinsed.

- After erection of pipe and tubing, but prior to installation of the service outlet valves, each system shall be blown clear of moisture and foreign matter by means of dry nitrogen or oil free air.

- After installing service outlet valves, each system shall be subjected to a test pressure of 150 psig by means of water-pumped (oil free) nitrogen or air.  This test pressure shall be maintained until each joint has been thoroughly examined for leaks by means of soapy water.  A soap solution mixed in the following proportions should be used:  one ounce of Castile or palm oil soap, eight ounces of water, and four ounces of glycerin.  Dissolve the soap in the water, add the glycerin and mix thoroughly.  Wipe joints clean after test.  All leaks shall be properly repaired and the system retested.

- A final test shall be 24 hours standing pressure test with water pumped (oil free) air or dry nitrogen at 150 psig to check the completeness of prior joint pressure tests.  If water pumped nitrogen is used, particular care must be exercised to assure that it is all flushed out with oxygen before placing the system in service.

- The piping systems shall be finally cleaned system cleaned using the high-pressure pulse-purge procedure described in NFPA 99.  During this procedure, sufficient volume of dry nitrogen shall be provided to insure a minimum velocity of 2000 fpm in the largest section of pipe being cleaned.  Note: It is not required that the entire system be tested at one time.  The system can be divided into convenient sections. Upon the successful completion of the operation on a section, it shall be sealed and left with a holding charge of dry nitrogen.

- Threaded joints shall be limited to connection to equipment and outlets.  Pipe threads shall conform to ANSI B1.20.I. Threaded joints shall be made using Teflon tape or other thread sealant recommended for oxygen service.

      - VALVES:

- Ball Valves: 3 Piece bronze ball valve with extended copper tube ends, 316 stainless steel ball and stem, 600 WOG, full port, in-line repairable, RPTFE seats, blow-out proof stem, manufactured by Milwaukee.  No. BA3055-TE, Nibco or Apollo.

- Check Valves: 3 piece, Type K copper tube extension ends, dual gauge/purge ports, cleaned for oxygen service, brass construction, rated of 300 psi working pressure, 100% hydrostatically tested manufactured by Amico “Alert 1” series , US Valve or Gentec.

      - LABORATORY FITTINGS:

Laboratory fittings will be furnished to the job site by the Laboratory Equipment Supplier, with necessary holes cut in the laboratory equipment.  The Contractor shall receive, store, and install the fittings and make all necessary connections thereto.

- EXECUTION

- INSTALLATION

- Install equipment in accordance with manufacturer's instructions.

- Install compressor units’ dryers and air receivers on a concrete housekeeping pad.  Refer to Section 22 00 00.

- Install compressor units on vibration isolators.  Level and bolt in place.  Refer to Section 22 05 48.

- Make air cock and drain connection on horizontal casing.

- Install line size gate or ball valve (depending on size), and a check valve on compressor discharge.

- Install replaceable cartridge type filter silencer of adequate capacity for each compressor.

- Place shut off valve on water inlet to aftercooler.  Pipe drain to floor drain.

- Connect condensate drains to nearest floor drain.

- Install valved bypass around air dryer.  Factory insulate inlet and outlet connections.

- Install valved drip connections at low points of piping system.

- Install take offs to outlets from top of main, with shut off valve after take off.  Slope take-off piping to outlets.

- Install compressed air couplings, female quick connectors, and pressure gauges where outlets are indicated.

- Install tees instead of elbows at changes in direction of piping.  Fit open end of each tee with plug.

- Identify and label piping system and components.  Refer to Section 22 05 53.

- Provide flex connector on the air compressor intake and outlet piping, isolate filter housing from the intake manifold with a flex connector.

- The air compressor shall draw air from a source of clean air located where no contamination from engine exhausts, fuel storage vents, plumbing vents, building exhausts etc., occur.  The air intake shall be a minimum distance of 25’ from any door, window, exhaust or vent and a minimum distance of 20’ above grade.  The intake terminal shall be turned down and a stainless steel screen secured over the terminal point with adjustable stainless steel bands.

- FIELD QUALITY CONTROL

- Field inspection and testing will be performed under provisions of Section 22 00 00 (including Uniform General Conditions as referenced therein), and Section 22 13 16.

- Compressed Air Piping Leak Test: Prior to initial operation, clean and test compressed air piping in accordance with ANSI B31.1.

- Repair or replace compressed air piping as required to eliminate leaks, and retest to demonstrate compliance.

- Cap (seal) ends of piping when not connected to equipment.

- STARTUP SERVICE

- Engage a factory authorized service representative to perform startup service.

Complete installation and startup, checks according to manufacturers’ written instructions.

Verify that all filters and piping are clean.

Lubricate all devices requiring lubrication.

Check all belts for proper tension.

Check equipment vibration control supports and flex pipe connectors and verify all equipment is properly attaches to substrate.

Check safety valve for correct settings

Drain receiver tanks.

Perform operational tests after electrical circuitry has been energized and start units to confirm proper performance.

Test and adjust all controls and safeties.

END OF SECTION 22 15 13