|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 www.uth.edu |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 23 05 13

MOTORS

To receive current updates of standard specification Sections, please go to the web site at: http://www.uth.edu or contact the Office of Facilities Planning and Engineering

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | October 2022 | 6 | Issuance |

SECTION 23 05 13 – motors

GENERAL

The following sections are to be included as if written herein:

Section 23 00 00 – Basic Mechanical Requirements

Section 23 05 29 – Sleeves, Flashings, Supports and Anchors

Section 23 05 53 – Mechanical Identification

SECTION INCLUDES

Single phase electric motors

Three phase electric motors

The Contractor shall provide all motors required for equipment supplied under this Division of the work

RELATED WORK

Section 23 22 00.A - Steam and Steam Condensate Specialties:  Condensate pumps

Section 23 20 00 - HVAC Pumps

Section 23 81 23 - Computer Room Air Conditioning Units

Section 23 82 19 - Terminal Heat Transfer Units:  Unit heaters, fan-coil units, and unit ventilators

Section 23 73 00 - Air Handling Unit with Coils (Up to 10,000 CFM):  Fan motors

Section 23 73 23 - Air Handling Unit:  Fan motors

Section 23 34 16 - Fans

REFERENCES

AFBMA 9 - Load Ratings and Fatigue Life for Ball Bearings

AFBMA 11 - Load Ratings and Fatigue Life for Roller Bearings

ANSI/IEEE 112 - Test Procedure for Polyphase Induction Motors and Generators

ANSI/NEMA MG 1 - Motors and Generators

ANSI/NFPA 70 - National Electrical Code

SUBMITTALS

Submit product data under provisions of Section 23 00 00

Submit test results verifying nominal efficiency and power factor for motors 1 horsepower and larger.

Submit manufacturer's installation instructions under provisions of Section 23 00 00

OPERATION AND MAINTENANCE DATA

Submit operation and maintenance data under provisions of Section 23 00 00

Include assembly drawings, bearing data including replacement sizes, and lubrication instructions.

QUALIFICATIONS

- Manufacturer:  Company specializing in manufacture of electric motors for commercial use, and their accessories, with minimum three years documented product development, testing, and manufacturing experience.

Baldor

Century/Gould

General Electric

Louis Allis

Reliance

Siemans-Allis

US Motors

Westinghouse

REGULATORY REQUIREMENTS

Conform to ANSI/NFPA 70.

DELIVERY, STORAGE, AND HANDLING

Deliver products to site under provisions of Section 23 00 00.

Store and protect products under provisions of Section 23 00 00.

Protect motors stored on site from weather and moisture by maintaining factory covers and suitable weather-proof covering.  For extended outdoor storage, remove motors from equipment and store separately.

WARRANTY

Provide five years manufacturer's warranty under provisions of Section 23 00 00.

Warranty:  Include coverage for motors 1 horsepower and larger.

PRODUCTS

GENERAL CONSTRUCTION AND REQUIREMENTS

Open Design Motors:  Design for continuous operation in 40 degrees C environment, and for temperature rise in accordance with ANSI/NEMA MG 1 limits for insulation class, Service Factor, and motor enclosure type.

Totally Enclosed Motors:   Design for a service factor of 1.00 and an 80 degrees C maximum temperature rise in the same conditions.

Explosion-Proof Motors:  UL approved and labeled for hazard classification, with over temperature protection.

Visible Nameplate:  Indicating motor horsepower, voltage, phase, cycles, RPM, full load amps, locked rotor amps, frame size, manufacturer's name and model number, Service Factor, Power Factor, efficiency.

Electrical Connection:  Conduit connection boxes, threaded for conduit.  For fractional horsepower motors where connection is made directly, provide threaded conduit connection in end frame.

Motors shall be built in accordance with the latest ANSI, IEEE, and NEMA Standards, and shall be fully coordinated with the equipment served, shall be of sizes and electrical characteristics scheduled, and of approved manufacture as described herein or of the same manufacture as the equipment which they serve.  All motors provided by the Contractor shall be of the same manufacture unless they are an integral part of the piece of equipment to which they are attached.  Nameplate rating of motors shall match the characteristics scheduled.

All motors shall be designed for NEMA Design B starting torque unless the driven machine requires high starting torque and shall be selected for quiet operation, free from magnetic hum.

In addition, all motors shall be provided with adequately sized electrical connection box with threaded hub for attachment of flexible conduit, unless bus duct connection is indicated.  Where motors are connected to driven equipment by the use of a V-belt drive, they shall be furnished with adjustable rails.

Dynamic Balance shall be no greater than the vibration limits of the driven equipment.

All motors shall be provided with all copper windings, terminal wiring, and copper or bronze lugs.  AL/CU rated connectors are not allowed.

SINGLE PHASE POWER - SPLIT PHASE MOTORS

Starting Torque:  Less than 150 percent of full load torque.

Starting Current:  Up to seven times full load current.

Breakdown Torque:  Approximately 200 percent of full load torque.

Drip-proof Enclosure:  Class A (50 degrees C temperature rise) insulation, NEMA Service Factor, pre-lubricated sleeve or ball bearings.

Enclosed Motors:  Class A (50 degrees C temperature rise) insulation, 1.0 Service Factor, pre-lubricated ball bearings.

Single phase motors, in general, shall be less than 3/4 horsepower and shall be permanent split phase, capacitor start, induction run, 120 volt, 60 hertz motors with drip-proof enclosures except as hereinafter specified.  These motors shall have built-in thermal overload protection with automatic reset, and shall be rated for temperature rise as hereinbefore specified for 3-phase motors.

SINGLE PHASE POWER - PERMANENT-SPLIT CAPACITOR Motors

Starting Torque:  Exceeding one fourth of full load torque.

Starting Current:  Up to six times full load current.

Multiple Speed:  Through tapped windings.

Open Drip-proof or Enclosed Air Over Enclosure:  Class A (50 degrees C temperature rise) insulation, minimum 1.0 Service Factor, pre-lubricated sleeve or ball bearings, automatic reset overload protector.

Single phase motors, in general, shall be less than 3/4 horsepower and shall be permanent split phase, capacitor start, induction run, 120 volt, 60 hertz motors.  These motors shall have built-in thermal overload protection with automatic reset, and shall be rated for temperature rise as hereinbefore specified for 3-phase motors.

SINGLE PHASE POWER - CAPACITOR START MOTORS

Starting Torque:  Three times full load torque.

Starting Current:  Less than five times full load current.

Pull-up Torque:  Up to 350 percent of full load torque.

Breakdown Torque:  Approximately 250 percent of full load torque.

Motors:  Capacitor in series with starting winding; capacitor-start/capacitor-run motors shall have two capacitors in parallel with run capacitor remaining in circuit at operating speeds.

Enclosures shall be of the open drip-proof type with a service factor of 1.15 and Class B insulation rated at 90 degrees C temperature rise measured above 40 degrees C room ambient condition at full load, unless otherwise noted.

Enclosed Motors:  Class A (50 degrees C temperature rise) insulation, 1.0 Service Factor, pre-lubricated ball bearings.

Single phase motors, in general, shall be less than 3/4 horsepower and shall be permanent split phase, capacitor start, induction run, 120 volt, 60 hertz motors.  These motors shall have built-in thermal overload protection with automatic reset, and shall be rated for temperature rise as hereinbefore specified for 3-phase motors.

THREE PHASE POWER - SQUIRREL CAGE MOTORS

Acceptable Manufacturers:  Subject to conformance with these specifications, furnish motors by one of the following manufacturers:

Baldor

TECO/Westinghouse

Toshiba

General Electric

In general, all motors 3/4 horsepower and larger, unless smaller motors are indicated to be supplied as 3-phase, shall be 3-phase and shall be squirrel cage premium efficiency induction type with standard NEMA frame sizes.

All three phase motors shall be inverter duty rated and equipped with a shaft grounding device.  Inverter duty motors shall be capable of withstanding repeated peaks of 1600 volts at 0.1 microsecond rise time and comply with NEMA MG-1 Part 31.

Motors 1 HP and larger shall have integral frames.

Starting Torque:  Between one and one and one-half times full load torque.

Starting Current:  Six times full load current.

Power Output, Locked Rotor Torque, Breakdown or Pullout Torque:  NEMA Design B Characteristics.

Design, Construction, Testing, and Performance:  Conform to ANSI/NEMA MG 1 for Design B motors.

Insulation System:  NEMA Class B or better.

Testing Procedure:  In accordance with ANSI/IEEE 112, Test Method B.  Load test motors to determine freedom from electrical or mechanical defects and compliance with performance data.  Test and balance motors to limits defined in 2.01J.

Motor Frames:  NEMA standard T-frames of steel, aluminum, or cast iron with end brackets of cast iron or aluminum with steel inserts.

Thermistor System (Motor Frame Sizes 254T and Larger):   Three PTC thermistors imbedded in motor windings and epoxy encapsulated solid state control relay for wiring into motor starter or VFD; refer to Division 26 for Starter Requirements.  Refer to Specification Section 23 29 23 for Variable Frequency Drives.

Bearings:  Ball or roller type, double shielded with continuous grease relief to accommodate excessive pressure caused by thermal expansion or over lubrication.  All motor bearings shall be factory pre-packed with a non-detergent lubricant, and shall be provided with lubrication fitting arranged to provide easy access when installed on the driven apparatus except as noted hereinafter.  Permanently lubricated factory-sealed motors may be provided in fractional HP sizes only where they are an integral part of a piece of approved apparatus.  All bearings shall be designed for L-10, 200,000 hours minimum life hours of continuous service.  Calculate bearing load with NEMA minimum V- belt pulley with belt center line at end of NEMA standard shaft extension.  Stamp bearing sizes on nameplate.

Sound Power Levels:  Refer to ANSI/NEMA MG 1.

Weatherproof Epoxy Treated Motors (Where Indicated):  Epoxy coat windings with rotor and starter surfaces protected with epoxy enamel.  Bearings shall be double shielded with waterproof non-washing grease.

Nominal Efficiency:  Furnish all motors with minimum efficiency equal to or greater than Efficiency Level of Premium Efficiency Motors as defined in the latest version of NEMA MG-1.

Service Factor:  M Furnish all motors with service factor equal to or greater than that required in the latest version of NEMA MG-1

Motors 1 HP and larger shall be provided with a copper frame grounding lug of hydraulic compression design, for installation by the electrical subcontractor.

Motors 3/4 HP and larger shall have 120V space heater that is energized only when motor is idle and subject to high humidity/dew point ,unconditioned or salt environments.

EXECUTION

APPLICATION

Motors drawing less than 250 Watts and intended for intermittent service may be germane to equipment manufacturer and need not conform to these specifications.

Motors shall be open drip-proof type, unless specified otherwise.

Single phase motors for [shaft mounted fans] [oil burners] [centrifugal pumps] shall be split phase type.

Single phase motors for shaft mounted fans or blowers shall be permanent split capacitor type.

Single phase motors for [fans] [pumps] [blowers] [air compressors] shall be capacitor start type.

Single phase motors for [fans] [blowers] [pumps] shall be capacitor start, capacitor run type.

Motors located in [exterior locations] [wet air streams downstream of sprayed coil dehumidifiers] [air-cooled condensers] [humidifiers] [direct drive axial fans] [roll filters] [explosion proof environments] [dust collection systems] [_______________] shall be totally enclosed type.

Motors located in [exterior locations] [wet air streams downstream of sprayed coil dehumidifiers] [draw thru cooling towers] [humidifiers] [_______________] shall be totally enclosed weatherproof epoxy-treated type.

END OF SECTION 23 05 13