|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 www.uth.edu |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 23 05 16

EXPANSION COMPENSATION

To receive current updates of standard specification Sections, please go to the web site at: http://www.uth.edu or contact the Office of Facilities Planning and Engineering

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | October 2022 | 6 | Issuance |

SECTION 23 05 16 – EXPANSION COMPENSATION

GENERAL

The following sections are to be included as if written herein:

Section 23 00 00 – Basic Mechanical Requirements

Section 23 05 29 – Sleeves, Flashings, Supports and Anchors

Section 23 05 53 – Mechanical Identification

Section 23 20 00.A – Pipes, Valves, and Fittings

SECTION INCLUDES

Flexible pipe connectors

Expansion joints and compensators

Pipe loops, offsets, and swing joints

RELATED SECTIONS

Section 23 21 00 - Hydronic Pumping

Section 23 22 00 - Steam and Steam Condensate Piping

Section 23 23 00 - Refrigerant Piping and Specialties

PERFORMANCE REQUIREMENTS

Provide structural work and equipment required to control expansion and contraction of piping.  Verify that anchors, guides, and expansion joints provided, adequately protect system.

Expansion Calculations:

Installation Temperature:  50 degrees F.

Chilled water: 42 degrees F.

Heating Hot Water:  210 degrees F.

Safety Factory:  30 percent.

SUBMITTALS

Submit under provisions of Section 23 00 00

Product Data:

Flexible Pipe Connectors:  Indicate maximum temperature and pressure rating, face-to-face length, live length, hose wall thickness, hose convolutions per foot and per assembly, fundamental frequency of assembly, braid structure, and total number of wires in braid.

Expansion Joints:  Indicate maximum temperature and pressure rating, and maximum expansion compensation.

Samples:  Submit two low pressure compensators 1 inch in size.

Design Data:  Indicate selection calculations.

Manufacturer's Installation Instructions:  Indicate special procedures, and external controls.

PROJECT RECORD DOCUMENTS

Submit under provisions of Section 23 00 00.

Record actual locations of flexible pipe connectors, expansion joints, anchors, and guides.

OPERATION AND MAINTENANCE DATA

Submit under provisions of Section 23 00 00.

Maintenance Data:  Include adjustment instructions.

QUALIFICATIONS

Manufacturer: Company specializing in manufacturing the products specified in this section with minimum three years documented experience.

Design expansion compensating system under direct supervision of a Professional Engineer experienced in design of this work and licensed in the State of Texas.

DELIVERY, STORAGE, AND HANDLING

Deliver, store, protect and handle products to site under provisions of Section 23 00 00.

Accept expansion joints on site in factory packing with shipping bars and positioning devices intact.  Inspect for damage.

Protect equipment from exposure by leaving factory coverings, pipe end protection, and packaging in place until installation.

WARRANTY

Provide five-year warranty.

Warranty:  Include coverage for leak free performance of packed expansion joints.

EXTRA MATERIALS

Provide two 12 ounce containers of packing lubricant and cartridge style grease gun.

PRODUCTS

FLEXIBLE PIPE CONNECTORS

Steel Piping:

Manufacturers:

Metraflex

Flex-Weld

Flexicraft

Inner Hose:  ASTM Grade 304, 316, or 321 Stainless Steel.

Exterior Sleeve:  Double braided ASTM Grade 304, 316, or 321 stainless steel.

Pressure Rating: 150 psig WOG at 250 degrees F for circulating water systems; 125 SWP at 400 F for steam

Joint:  As specified for pipe joints.

Size:  Use pipe sized units.

Maximum offset:  3/4 inch on each side of installed center line.

Application: Pump connections and vibration isolating connections on steel circulating water systems.

Single/Double Flexible Sphere :

Manufacturers:

Metraflex

Flex-Weld

Kinetics Noise Control

Body: EPDM (Teflon)

Working Pressure:  225 psi at 170 F

Maximum Temperature:  225 degrees F.

Maximum Compression: Single sphere: 1/2 inch; double sphere: 1 3/4 inches

Maximum Elongation:  Single sphere: 1/8 inch; double sphere: 1/2 inch

Maximum Offset:  Single sphere: 3/8 inch; double sphere: 3/4 inch

Maximum Angular Movement:  15 degrees.

Joint:  As specified for pipe joints.

Size:  Use pipe sized units.

Accessories:  Control rods or control cables to prevent overextension

Application: Pump connections and vibration isolating connections on circulating water systems.

Copper Piping:

Manufacturers:

Metraflex

Flex-Weld

Flexicraft

Inner Hose:  Bronze

Exterior Sleeve:  Double-braided bronze.

Pressure Rating: 150 psig WOG and 250 degrees F.

Joint:  As specified for pipe joints.

Size:  Use pipe sized units.

Maximum offset:  3/4 inch on each side of installed center line.

Application: Pump connections and vibration isolating connections on copper circulating water systems.

Flexible hose expansion loops

General Requirements:

All flexible pipe connectors shall be double braided.

Stainless steel flexible pipe connectors shall be used with steel pipe; bronze flexible pipe connectors shall be used with copper pipe.

Flexible hose expansion loops shall be manufactured complete. Field fabricated loops are not acceptable.

Flexible hose expansion loop shall impart no thrust loads to system supports, anchors, or the building structure.

All flexible hose expansion loops shall be manufactured in accordance with ASME BPVC Section IX.

Flexible expansion loops shall have a factory supplied, hanger/support lug located at the bottom of the 180 degree return.

Flexible expansion loops shall be furnished with a plugged FPT fitting for a vent or drain. For pipes 1”—6”, the fitting shall be 3/8” FPT; for pipes 8” and larger, the fitting shall be ½” FPT.

On steam systems, hose shall be installed horizontally with a drip leg and steam trap upstream of compensator.

Piping:

Manufacturers:

Metraflex

Flex-Weld

Flexicraft

Inner Hose:  ASTM Grade 304, 316, or 321 Stainless Steel.

Exterior Sleeve:  Double braided ASTM Grade 304, 316, or 321 stainless steel.

Pressure Rating: 150 psig WOG at 250 degrees F for circulating water systems; 125 SWP at 400 F for steam

Joint:  As specified for pipe joints.

Size:  Use pipe sized units.

Maximum offset:  3/4 inch on each side of installed center line.

Application: steel circulating water systems and low and medium pressure steam systems.

Copper Piping:

Manufacturers:

Metraflex

Flex-Weld

Flexicraft

Inner Hose:  Bronze

Exterior Sleeve:  Double-braided bronze.

Pressure Rating: 150 psig WOG and 250 degrees F.

Joint:  As specified for pipe joints.

Size:  Use pipe sized units.

Maximum offset:  3/4 inch on each side of installed center line.

Application: copper circulating water systems.

EXPANSION JOINTS

Stainless Steel Bellows Type: Manufacturers:

Metraflex

Unaflex

Flex-Weld

Flexicraft

Bellows material shall be ASTM Grade 304, 316, or 321.

Pressure Rating: 125 psig WSP and 400 degrees F for low and medium pressure steam; 150 psig WOG and 250 degrees F for circulating water.

Maximum Compression: 1 1/2”

Maximum Extension:  1/4”.

Joint:  As specified for pipe joints.

Size:  Use pipe sized units.

Application:  Steel piping 3 inch and under where expected thermal expansion is less than 1 ½”. When used for chilled water, bellows shall be preloaded to expected contraction distance per expansion calculations.

ACCESSORIES

Pipe Alignment Guides:

Manufacturers:

Metraflex

Flexicraft

Twin City Hose, Inc.

Two piece welded steel with enamel paint, bolted, with spider to fit standard pipe, frame with four mounting holes, clearance for minimum 1 inch thick insulation, minimum 3 inch travel.

EXECUTION

INSTALLATION

Install in accordance with manufacturer's instructions.

Construct spool pieces to exact size of flexible connection for future insertion.

Install flexible pipe connectors on pipes connected to equipment supported by vibration isolation.  Provide line size flexible connectors.

Install flexible connectors at right angles to displacement. Install one end immediately adjacent to isolated equipment and anchor other end. Install in horizontal plane unless indicated otherwise.

Rigidly anchor pipe to building structure where necessary.  Provide pipe guides so movement is directed along axis of pipe only. Erect piping such that strain and weight is not on cast connections or apparatus.

Provide support and equipment required to control expansion and contraction of piping.  Provide loops, pipe offsets, and swing joints, or expansion joints where indicated.

Provide expansion loops as indicated on drawings.

MANUFACTURER'S FIELD SERVICES

Prepare and start systems under provisions of Section 23 00 00.

Provide inspection services by flexible pipe manufacturer's representative for final installing and certify installation is in accordance with manufacturer's recommendations and connectors are performing satisfactorily.

END OF SECTION 23 05 16