|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 www.uth.edu |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 23 05 29

SLEEVES, FLASHING, SUPPORTS, AND ANCHORS

To receive current updates of standard specification Sections, please go to the web site at: http://www.uth.edu or contact the Office of Facilities Planning and Engineering

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | October 2022 | 11 | Issuance |

SECTION 23 05 29 – SLEEVES, FLASHINGS, SUPPORTS, AND ANCHORS

GENERAL

THE FOLLOWING SECTIONS ARE TO BE INCLUDED AS IF WRITTEN HEREIN:

Section 23 00 00 – Basic Mechanical Requirements

Section 23 05 53 – Mechanical Identification

SECTION INCLUDES

Pipe and equipment hangers and supports

Equipment bases and supports

Sleeves and seals

Flashing and sealing equipment and pipe stacks

PRODUCTS FURNISHED BUT NOT INSTALLED UNDER THIS SECTION

Section [_____ __________]:  Placement of [inserts] [sleeves] in concrete formwork.

Section [_____ __________]:  Placement of roofing [pipe] [duct] supports.

Section [_____ __________]:  Placement of equipment roof supports.

Section [_____ __________]:  Placement of roof sleeves, vents, and curbs.

PRODUCTS INSTALLED BUT NOT FURNISHED UNDER THIS SECTION

Section [_____ __________]:  Supply of roofing [pipe] [duct] [equipment] supports for placement by this Section.

RELATED SECTIONS

Section 03300   Cast In Place Concrete:  Equipment bases

Section 07 84 00   Firestopping:  Joint seals for piping and duct penetration of fire rated assemblies

Section 09 91 00   Painting

Section 23 05 4   Vibration Isolation

Section 23 07 19   Piping Insulation

Section 23 07 16   Equipment Insulation

Section 23 07 16   Ductwork Insulation

Section 23 21 00   Hydronic Piping

Section 23 22 00   Steam and Steam Condensate Piping

REFERENCES

ASME B31.1   Power Piping

ASME B31.5   Refrigeration Piping

ASME B31.9   Building Services Piping

ASTM F708   Design and Installation of Rigid Pipe Hangers

MSS SP58   Pipe Hangers and Supports Materials, Design and Manufacturer

MSS SP69   Pipe Hangers and Supports Selection and Application

MSS SP89   Pipe Hangers and Supports Fabrication and Installation Practices

SUBMITTALS

Submit under provisions of Section 23 00 00.

Shop Drawings:  Indicate system layout with location and detail of trapeze hangers.

Product Data:  Provide manufacturers catalog data including load capacity.

Design Data:  Indicate load carrying capacity of trapeze, multiple pipe, and riser support hangers.

Manufacturer's Installation Instructions:  Indicate special procedures and assembly of components.

REGULATORY REQUIREMENTS

Conform to applicable code for support of hydronic, steam and steam condensate piping.

PRODUCTS

HANGERS AND SUPPORTS

Manufacturers:

Anvil

Kindorf

B-Line

Power Strut

Other acceptable manufacturers offering equivalent products.

[_____________________________] Model [________].

[_____________________________] Model [________].

[_____________________________] Model [________].

Supports, hangers, anchors and guides shall be provided for all horizontal and vertical piping.  Shop Drawings shall be provided, indicating locations and details of anchors, guides, expansion loops and joints, hangers, etc.  The hanger design shall conform to the ASME Code for Pressure Piping.

All auxiliary steel required for supports, anchors, guides, etc. shall be provided by the Mechanical Trades unless specifically indicated to be provided by others.

The supports, hangers, anchors, and guides for the chilled water supply and return piping, steam piping, condensate return piping, etc. of the Campus Loop System routed through utility tunnels and below buildings shall be provided as indicated on the Drawings.

Contractor shall review all Drawings, including Structural Drawings, for details regarding pipe supports, anchors, hangers, and guides.

All Supports shall be of type and arrangement to prevent excessive deflection, to avoid excessive bending stresses between supports, and to eliminate transmission of vibration.

All rod sizes indicated in this Specification are minimum sizes only.  This trade shall be responsible for structural integrity of all supports, anchors, guides, etc.  All structural hanging materials shall have a minimum safety factor of 5 built in.

Anchor points as indicated on Drawings or as required shall be located and constructed to permit the piping system to take up its expansion and contraction freely in opposite directions away from the anchored points.

Guide points shall be located and constructed wherever required or indicated on Drawings and at each side of an expansion joint or loop, to permit free axial movement only.

Supports, hangers, anchors, and guides shall be fastened to the structure only at such points where the structure is capable of restraining the forces in the piping system.

Hangers supporting and contacting brass or copper lines 3" in size and smaller shall be Anvil Fig. CT-65 adjustable, copper plated, clevis hanger.  Hangers supporting and contacting brass or copper lines 4" and larger shall be Anvil Fig. 260, adjustable clevis, with a nut above and below the hanger, and approved neoprene isolating material between pipe (or tubing) and hanger on the support rod.  For insulated copper or brass domestic water lines, hangers for all sizes of pipe shall be Anvil Fig. 300, adjustable clevis, with a nut above and below the hanger, and approved neoprene isolating material between pipe (or tubing) and hanger on the support rod.  Isolate all copper or brass lines from all ferrous materials with approved dielectric materials.  Hangers supporting and contacting plastic or glass piping shall be of equal design, but shall be padded with neoprene material or equal.  The padding material and the configuration of its installation shall be submitted for approval.

Hangers supporting insulated lines where the outside diameter of the insulation is the equivalent of 8" diameter pipe or smaller in size and supporting all ferrous lines 6" and smaller in size shall be Anvil Fig. 260, adjustable clevis, with a nut above and below the hanger on the support rod.

Hangers supporting and contacting ferrous lines larger than 6" in size and outside of insulation on lines with the outside diameter equivalent to 10" diameter pipe shall be Anvil Fig. 260, adjustable clevis, with a nut above and below the hanger on the support rod.

Other special type of hangers may be employed where so specified or indicated on the Drawings, or where required by the particular conditions.  In any case, all hangers must be acceptable to the owner.

Each hanger shall be properly sized to fit the supported pipe or fit the outside of the insulation on lines where specified.  Hangers for dual or low temperature insulation pipes shall bear on the outside of the insulation, which shall be protected by support shields as specified in Section 23 07 19    PIPING INSULATION.  Protect insulation from crushing by means of a section of rigid insulation to be installed at hanger points.  Hangers for high temperature insulated pipes and all insulated hot and cold domestic water pipes shall be encased in the insulation unless supported by trapezes in which case shield and rigid insulation shall be provided as specified above for low temperature insulated pipes.

Supports for vertical piping in concealed areas shall be double bolt riser clamps, Anvil Fig. 261, or other approved equal, with each end having equal bearing on the building structure, and located at each floor.  Two hole rigid pipe clamps at 4 ft. o.c. or Kindorf channels and Anvil Fig. 261 riser clamps may be used to support pipe directly from vertical surfaces or members where lines are not subject to expansion and contraction.  When piping is subject to expansion and contraction, provide spring isolators (see Section 23 05 48 - Vibration Isolation).  Where brass or copper lines are supported on trapeze hangers or Kindorf channels the pipes shall be isolated from these supports with plastic tape with insulating qualities, or strut clamps as manufactured by Specialty Products Company, Stanton, California.

Supports for vertical piping in exposed areas (such as fire protection standpipe in stairwells) shall be attached to the underside of the building structure above the top of the riser, and the underside of the penetrated structure.  The contractor shall use a drilled anchor as specified above, and use an Anvil No. 595 Socket Clamp with Anvil No. 594 Socket Clamp Washers, as a riser clamp.  The top riser hanger shall consist of two (2) hanger rods (sized as specified) anchored to the underside of the building structure, supporting the pipe by means of the material specified.  Risers penetrating floors shall be supported from the underside of the penetrated floor as specified for the top of the riser.

Pipe Supports in Chases and Partitions:  Horizontal and vertical piping in chases and partitions shall be supported by hangers or other suitable support.  Pipes serving plumbing fixtures and equipment shall be securely supported near the point where pipes penetrate the finish wall.  Supports shall be steel plate, angles, or special channels such as Unistrut mounted in vertical or horizontal position.  Pipe clamps such as Unistrut P2426, P2008, P1109 or other approved clamps shall be attached to supports.  Supports shall be attached to wall or floor construction with clip angles, brackets, or other approved method.  Supports may be attached to cast iron pipe with pipe clamp, or other approved method.  All copper or brass lines shall be isolated from ferrous metals with dielectric materials to prevent electrolytic action.

Perforated strap iron or wire will not, under any circumstances, be acceptable as hanger material.

Vibration Isolation:  Resilient hangers shall be provided on all piping connected to rotating equipment (pumps, etc.).  Piping or ductwork that may vibrate and create an audible noise shall also be isolated.  Spring hangers or supports shall be provided where indicated on the Drawings and/or specified under Section 23 05 48.

Attachment:

The load and spacing on each hanger and/or insert shall not exceed the safe allowable load for any component of the support system, including the concrete which holds the inserts.  Reinforcement at inserts shall be provided as required to develop the strength required.

Inserts shall be of a type which will not interfere with reinforcing as shown on the structural Drawings and which will not displace excessive amounts of structural concrete.

All supports shall be designed and installed to avoid interference with other piping, hangers, ducts, electrical conduit, supports, building structures, equipment, etc.  All piping shall be installed with due regard to expansion and contraction and the type of hanger method of support, location of support, etc. shall be governed in part by this Specification.

Hangers shall be attached to the structure as follows:

Poured In Place Concrete:  Where pipes and equipment are supported under poured in place concrete construction, each hanger rod shall be fitted with a nut at its upper end, which nut shall be set into an Underwriters Laboratories, Inc. listed universal concrete insert placed in the form work before concrete is poured.  Where inserts are placed in the bottom faces of concrete joists which are too narrow to provide adequate strength of concrete to hold the insert properly or where a larger insert would require displacement of the bottom joist steel, the hanger rod shall be suspended from the center of a horizontal angle iron, channel iron, I beam, etc. spanning across two adjacent joists.  The horizontal support shall be bolted to nonadjustable concrete inserts of the "spot" type, of physical size small enough to avoid the bottom joist steel.

Steel Bar Joists:  Where pipes and loads are supported under bar joists, hanger rods may be run through the space between the bottom angles and secured with a washer and two nuts.  Where larger lines are supported beneath bar joists, hanger rods shall be secured to angle irons of adequate size; each angle shall span across two or more joists as required to distribute the weight properly and shall be welded to the joists or otherwise permanently fixed thereto.

Steel Beams:  Where pipes and loads are supported under steel beams, approved type beam clamps shall be used.

Wood Framing:  Where pipes and loads are supported from wood framing, hanger rods shall be attached to framing with side beam brackets or angle clips.

Pre Cast Tee Structural Concrete:  Hanger supports, anchors, etc. required for mechanical systems attached to the precast, double tee, structural concrete system are to be installed in accord with approved shop Drawings only.  Holes required for hanger rods shall be core drilled in the "flange" of the double tee only; impact type tools are not allowed under any circumstances.  Core drilling in the "stem" portions of the double tee is not allowed.  Holes core drilled through the "flange" for hanger rods shall be no greater than 1/4" larger than the diameter of the hanger rod.  Hanger rods shall be supported by means of bearing plates of size and shape acceptable to the Architect/Engineer, with welded double nuts on the hanger rod above the bearing plate.  Cinch anchors, lead shields, expansion bolts, and studs driven by explosion charges are not allowed under any circumstances in the lower 15" of each stem and in the "shadow" of the stem on the top side of the "double tees.”

If it is necessary to install a method of fastening a hanger after the structure has been installed, then only clamps or drilled anchors shall be used.

Note: Power actuated fasteners (shooting) will not be acceptable under any circumstances.

Note:  Under no circumstances will the use of plastic anchors or plastic expansion shields be permitted for any purpose whatsoever.

Trapezes:  Where multiple lines are run horizontally at the same elevation and grade, they may be supported on trapezes of Anvil, Kindorf, Uni-Strut, Power Strut, or approved equal, 1 5/8” x 1 5/8” channel suspended on rods or pipes.  Trapeze members including suspension rods shall each be properly sized for the number, size, and loaded weight of the lines they are to support.

Finishes:  All hangers on piping including clevis hangers, rods, inserts, clamps, stanchions, and brackets, shall be dipped in Zinc Chromate Primer before installation.  Rods may be galvanized or cadmium plated after threading, in lieu of dipping zinc chromate.  Universal concrete inserts shall be cadmium plated.

Ductwork:  All ductwork shall be supported in accordance with the SMACNA recommendation for the service involved; however, all horizontal ductwork shall be supported at intervals not to exceed the scheduled values indicated elsewhere in this section.  Horizontal ducts shall be supported using galvanized steel bands extending up both sides and onto the construction above, where they shall turn over and be secured with bolts and nuts fitted in inserts set in the concrete bolted to angles secured to the construction above, or secured in another approved manner.  For attaching methods for precast double tee structural concrete, refer to details on the Drawings and as specified herein.

Terminal units shall be supported by four 16 gauge, 1” wide sheet metal straps which shall be folded under the bottom of the casing a minimum of 1”. Attach each strap to bottom of terminal unit with two sheet metal screws not larger than ¾” in length and not more that ¼” in diameter. The straps shall be attached to the structure by a ¼” diameter threaded bolt into a concrete insert or into a drilled hole with a threaded concrete expansion anchor. Where interferences occur, overhead of the box, not allowing direct vertical support by straps, provide trapezes of Kindorf, Unistrut, or B-Line channel suspended by 3/8" diameter galvanized threaded rods providing such channels do not block access panels of boxes. Threaded rods shall be supported from structure by concrete insert or by drilled-hole threaded concrete expansion anchor.

Miscellaneous:  Provide any other special foundations, hangers and supports indicated on the Drawings, specified elsewhere herein; or required by conditions at the site.  Hangers and supporting structures for suspended equipment shall be provided as required to support the load from the building structure in a manner acceptable to the Architect/Engineer.

ACCESSORIES

Hanger Rods:  Galvanized mild steel threaded both ends, galvanized threaded one end, or galvanized continuous threaded. Hanger rods shall not be spliced.

Inserts:  Malleable iron case of galvanized steel shell and expander plug for threaded connection with lateral adjustment, top slot for reinforcing rods, lugs for attaching to forms; size inserts to suit threaded hanger rods.  Suitable concrete inserts for pipe and equipment hangers shall be set and properly located for all pipe and equipment to be suspended from concrete construction.  If the inserts are later found not to be in the proper location for the placement of hangers, then drilled anchors shall be installed.  Drilled anchors in concrete or masonry shall be submitted for the approval by the Owner.

FLASHING AND EQUIPMENT CURBS

Metal Flashing: 26 gauge galvanized (stainless steel) steel.

Metal Counterflashing: 22 gauge galvanized (stainless steel) steel.

Roofing Flashing: See specifications for Roofing, elsewhere in these Specifications.

Caps: Steel, 22 gauge minimum; 16 gauge at fire resistant elements.

Curbs: Welded 18 gauge galvanized steel shell and base, mitered 3 inch cant, variable step to match roof insulation, factory installed wood nailer.

CONCRETE FOUNDATIONS ("HOUSEKEEPING PADS"):

Concrete foundations for the support of equipment such as floor mounted panels, pumps, fans, air handling units, etc., shall extend 4" on all sides beyond the limits of the mounted equipment unless otherwise noted and shall be poured in forms built of new dressed 6" nominal lumber.  All corners of the foundations shall be neatly chamfered by means of sheet metal or triangular wood strips nailed to the form.  Foundation bolts shall be placed in the forms when the concrete is poured, the bolts being correctly located by means of templates.  Each bolt shall be set in a sleeve of size to provide 1/2" clearance around bolt.  Allow 1" below the equipment bases for alignment and grouting. After grouting, the forms shall be removed and the surface of the foundations shall be hand rubbed with carborundum. Foundations for equipment located on the exterior of the building shall be provided as indicated.  Foundations shall be constructed in accordance with Shop Drawings submitted by the Contractor for review by the Architect/Engineer.

WALL, FLOOR AND CEILING PLATES:

Except as otherwise noted, provide C.P. (Chrome plated) brass floor and ceiling plates around all pipes, conduits, etc., passing exposed through walls, floors, or ceilings, in any spaces except underfloor and attic spaces.  Plates shall be sized to fit snugly against the outside of the pipe or against the insulation on lines which are insulated and positively secured to such pipe or insulation.  Plates will not be required for piping where pipe sleeves extend 3/4" above finished floor.  All equipment rooms are classified as finished areas.  Round and rectangular ducts shall have closure plates (NOT chrome plated) made to fit accurately at all floor, wall and ceiling penetrations.  Floor penetrations in exposed (except in stair wells) areas shall be finished using 'bell' fitting to fit pipe or insulation and sleeve and shall be painted to match the pipe.  Penetrations in stairwells shall have flat floor plate painted to match pipe.

SLEEVES

General:  All openings through all floors, walls, and roofs, etc., regardless of material for the passage of piping, ductwork, conduit, cable trays, etc., shall be sleeved.  All penetrations must pass through sleeves.  Sleeves shall be set in new construction before concrete is poured, as cutting holes through any part of the concrete will not be permitted unless acceptable to the Architect/Engineer.  If a penetration is cored into an existing vertical solid concrete, masonry or stone structure, then the installation of a sleeve will not be necessary.

Sleeve material for floors and exterior walls shall be Schedule 40 galvanized steel with welded water stop rings.

Sleeves through interior walls to be galvanized sheetmetal with gauge as required by wall fire rating, 20 gauge minimum.

The minimum clearance between horizontal penetrations including insulation where applicable, and sleeve shall be 1/4", except that the minimum clearance shall accommodate a Thunderline Link seal closure where piping exits the building, or penetrates a wall below ground level.  Contractor shall be responsible for the accurate location of penetrations in the slab for his pipe, duct, etc.  All penetrations shall be of ample size to accommodate the pipe, duct, etc., plus any specified insulation.  Void between sleeve and pipe in interior penetrations shall be filled with Nelson Flameseal Firestop or approved equal caulk or putty.

Floor sleeves shall extend above the finished floor as detailed on the drawings, except that floor sleeves in stairwells shall be flush with the finished floor.  Sleeves in walls shall be trimmed flush with wall surface.  Refer to the details on the project drawings.  Where the details differ from these specifications, the drawings take precedence.

Sleeves for penetrations passing through walls or floors on or below grade shall be removed, if practical, and after the pipes have been installed, the void space around the pipe shall be caulked with a suitable material to effect a waterproof penetration.  Note that the practicality of the removal of the sleeve shall be the decision of the Construction Inspector.  The decision of the Inspector shall be final.

Vermin proofing:  The open space around all ductwork, piping, etc., passing through the ground floor and/or exterior walls shall be vermin proofed in a manner acceptable to the Architect/Engineer.

Waterproofing:  The annular space between a pipe and its sleeve in interior floors shall be filled with polyurethane foam rods 50 percent greater in diameter than the space as backing and fill material and made watertight with a permanent elastic polysulfide compound.  Seal both surfaces of floor.

Air Plenums:  The space around piping, ductwork, etc., passing through air plenums shall be made airtight in a manner acceptable to the Architect/Engineer.

Fireproofing:  Seal all cable trays, pipe, conduit, duct, etc., penetrations through roof, fire rated walls and floors with a foam or sealant as described below that will form a watertight, vermin tight barrier that is capable of containing smoke and fire up to 2000 F for two hours.  Sealing of cable trays and conduits that extend through rated walls from ends of cable tray shall be done after conductors have been installed.  For wet locations, the foam material shall be a silicone RTV foam or an approved equal.  For dry locations, a premixed putty equal to Nelson Flameseal Firestop putty may be used.

EXECUTION

INSTALLATION

Install in accordance with manufacturer's instructions.

INSERTS

Provide inserts for placement in concrete formwork.

Provide inserts for suspending hangers from reinforced concrete slabs and sides of reinforced concrete beams.

Provide hooked rod to concrete reinforcement section for inserts carrying pipe over 4 inches.

Where concrete slabs form finished ceiling, locate inserts flush with slab surface.

Where inserts are omitted, drill through concrete slab from below and provide through bolt with recessed square steel plate and nut recessed into and grouted flush with slab.

PIPE HANGERS AND SUPPORTS

Support horizontal piping as scheduled.

Install hangers to provide minimum 1/2 inch space between finished covering and adjacent work.

Place hangers within 12 inches of each horizontal elbow.

Use hangers with 1 1/2 inch minimum vertical adjustment.

Support horizontal cast iron pipe adjacent to each hub, with 5 feet maximum spacing between hangers.

Support vertical piping at every floor.  Support vertical cast iron pipe at each floor at hub.

Where several pipes can be installed in parallel and at same elevation, provide multiple or trapeze hangers.

Support riser piping independently of connected horizontal piping.

Provide copper plated hangers and supports for copper piping.

Design hangers for pipe movement without disengagement of supported pipe.

Prime coat exposed steel hangers and supports.  Hangers and supports located in crawl spaces, pipe shafts, and suspended ceiling spaces are not considered exposed, but shall be corrosion protected with galvanized plating.  Repair any damaged galvanized plating with a coating of 'Galvalum'.

Hanger Rods: (NOTE:  All hanger rods shall be trimmed neatly so that no more than 1 inch of excess hanger rod protrudes beyond the hanger nut.  In the event a rod is intentionally but temporarily left excessively long (for sloped or insulated lines for example), the contractor shall take appropriate measures to protect the pipe or other materials from damage.)

FLASHING

Provide flexible flashing and metal counterflashing where piping and ductwork penetrate weather or waterproofed walls, floors, and roofs.

Provide curbs for mechanical roof installations 14 inches minimum high above roofing surface.  Flash and counterflash with sheet metal; seal watertight.  Attach counterflashing mechanical equipment and lap base flashing on roof curbs.  Flatten and solder joints.

Adjust storm collars tight to pipe with bolts; caulk around top edge.  Use storm collars above roof jacks.  Screw vertical flange section to face of curb.

SLEEVES

Set sleeves in position in formwork.  Provide reinforcing around sleeves.

Size sleeves large enough to allow for movement due to expansion and contraction.  Provide for continuous insulation wrapping.

Extend sleeves through floors (except in stairwells) two inches above finished floor level.  Sleeves through floors shall have welded waterstop rings.  Sleeves shall be sealed watertight to floors and pipe.

Where piping, ductwork or conduit penetrates floor, ceiling, or wall, close space between pipe or duct and adjacent work with fire stopping insulation and caulk airtight.  Provide close fitting metal collar or escutcheon covers, as appropriate, at both sides of penetration.

Install chrome plated steel or stainless steel escutcheons at finished surfaces.

PIPE SUPPORT SCHEDULES

| STEEL PIPE SIZE Inches | MAX HANGER SPACING Feet | HANGER ROD DIAMETER Inches |
| --- | --- | --- |
| 1/2 to 1-1/4 | 6.5 | 3/8 |
| 1-1/2 to 2 | 10 | 3/8 |
| 2-1/2 to 3 | 10 | 1/2 |
| 4 to 6 | 10 | 5/8 |
| 8 to 12 | 14 | 7/8 |
| 14 and Over | 20 | 1 |

LOW PRESSURE DUCT SUPPORT SCHEDULE:

All horizontal ducts up to and including 40 inches in their greater dimension shall be supported by means of No. 18 U.S. gauge band iron hangers attached to the ducts by means of screws, rivets, or clamps and fastened to above inserts with toggle bolts, beam clamps or other approved means.  Duct shall have at least one pair of supports 8' 0" on centers.  Clamps shall be used to fasten hangers to reinforcing on sealed ducts.

Horizontal ducts larger than 40 inches in their greatest dimension shall be supported by means of hanger rods bolted to angle iron trapeze hangers.  Duct shall have at least one pair of supports 8' 0" on centers according to the following:

| Length | Angle | Rod Diameter |
| --- | --- | --- |
| 4’ 0" | 1-1/2" x 1-1/2" x 1/8" | 3/8" |
| 6' 0" | 1-1/2" x 1-1/2" x 1/8" | 3/8" |
| 8' 0" | 2" x 2" x 1/8" | 5/16" |
| 10' 0" | 3" x 3" x 1/8" | 3/4" |

Vertical ducts shall be supported where they pass through the floor lines with 1 1/2" x 1 1/2" x 1/4" angles for ducts up to 60.”  Above 60", the angles must be increased in strength and sized on an individual basis considering space requirements.

MEDIUM PRESSURE DUCT SUPPORT SCHEDULE:

All horizontal rectangular ducts shall have duct hanger requirements as follows:

| Minimum Hanger Size |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Max Duct Dimen. | Steel Rod | Galvanized Steel Strap Width | Max Spacing | Min # of Hangers | Trapeze Size |
| 0 through 18" | -- | 1" x 16 ga. | 10' | 2 | -- |
| 19" through 36" | -- | 1" x 16 ga. | 10' | 2 | -- |
| 37" through 60" | 3/8" | 1" x 16 ga. | 8' | 2 | 2" x 2" x 1/4" |
| 61" through 120" | 3/8" | 1-1/2" x 12 ga. | 8' | 2 | 2" x 2" x 1/4" |
| 121" through 240 | 3/8" | -- | 4' | 3 | 2-1/2" x 2-1/2" x 3/16" |

All horizontal round ducts shall have ducts hangers spaced 10' 0" maximum with requirements as follows:

| Duct Diameter | Min. Hanger Size | No. Hangers | Hanger Ring Size |
| --- | --- | --- | --- |
| Up through 18" | 1" x 16 gauge | 1 | 1" x 16 ga. |
| 19" to 36" | 1" x 12 gauge | 1 | 1" X 12 ga. |
| 37" to 50" | 1-1/2" x 12 gauge | 1 | 1-1/2" x 12 ga. |
| 51" to 84" | 1-1/2" x 12 gauge | 2 | Support Bracing Angle |

DUCT HANGERS - GENERAL NOTES (ALL PRESSURES)

Hanger straps on duct width of 60 inches and under shall lap under the duct a minimum of 1 inch and have minimum of two fastening screws on the bottom and two on the side.

Hanger straps on duct widths over 60 inches shall be bolted to duct reinforcing with 3/8" bolts minimum.

Use 3/8" minimum bolts for securing duct hanger to band straps.

All round ducts shall be supported within 3 feet of all horizontal or vertical turns.

END OF SECTION 23 05 29