|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 www.uth.edu |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 23 05 53

MECHANICAL IDENTIFICATION

To receive current updates of standard specification Sections, please go to the web site at: http://www.uth.edu or contact the Office of Facilities Planning and Engineering

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | October 2022 | 5 | Issuance |

SECTION 23 05 53 – piping and equipment identification

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General Conditions and Division 01 Specification Sections, apply to this Section.

Specifications throughout all Divisions of the Project Manual are directly applicable to this Section, and this Section is directly applicable to them.

SUMMARY

Perform all Work required to provide and install Owner’s equipment tags, fire damper tags, valve tags, stencils, and pipe markers indicated by the Contract Documents with supplementary items necessary for proper installation.

Contractor shall make it possible for Owner’s operations and maintenance personnel to readily identify the various pieces of equipment, valves, piping, ductwork, fire dampers etc., by marking them in accordance with this Specification.

Clearly mark all items of equipment, including but not limited to, fans, pumps, fire dampers, and valves using equipment tags as specified in this Section.  The tagged item of equipment shall correspond to the same number as shown on the Drawings and as listed in the Equipment Matrix.

REFERENCE STANDARDS

The latest published edition of a reference shall be applicable to this Project unless identified by a specific edition date.

All reference amendments adopted prior to the effective date of this Contract shall be applicable to this Project.

All materials, installation and Workmanship shall comply with the applicable requirements and standards addressed within the following references:

ASME A13.1 - Scheme for the Identification of Piping Systems.

SUBMITTALS

Product Data:

Provide manufacturer’s catalog literature for each product.

Record Documents:

Submit Equipment Matrix with Valve and Fire Damper schedules completed

Operation and Maintenance Data:

Manufacturer’s Installation Instructions:  Indicate special procedures and installation.

PRODUCTS

NAMEPLATES

Description:  Laminated three-layer plastic with engraved white letters on black background.

TAGS

Plastic Tags: Laminated three-layer plastic with engraved [black] [_____] letters on light contrasting background color.  Tag size minimum 1-1/2 inch (40 mm) [diameter] [square] [_________].

********** [OR] *********

Metal Tags: [Brass] [Aluminum] [Stainless Steel] [__________] with stamped letters; tag size minimum 1-1/2 inch (40 mm) [diameter] [square] [______] with smooth edges.

Chart:  Typewritten letter size list in anodized aluminum frame.

PIPE MARKERS

Manufacturers:

Color: Conform to ASME A13.1.

Plastic Pipe Markers: Factory fabricated, flexible, semi- rigid plastic, preformed to fit around pipe or pipe covering; minimum information indicating flow direction arrow and identification of fluid being conveyed.

Underground Plastic Pipe Markers: Bright colored continuously printed plastic ribbon tape, minimum 6 inches (150 mm) wide by 4 mil (0.10 mm) thick, manufactured for direct burial service.

CEILING TACKS

Manufacturers:

[_________________________________] Model [________].

Other acceptable manufacturers offering equivalent products.

[_____________________________] Model [________].

[_____________________________] Model [________].

[_____________________________] Model [________].

Description:  Steel with 7/8 inch (20 mm) diameter color coded head.

Color code as follows:

Yellow - HVAC equipment

Red    - Fire dampers/smoke dampers

Green - Plumbing valves

Blue   - Heating/cooling valves

General:

The Contractor shall make it possible for the personnel operating and maintaining the equipment and systems in this project to readily identify the various pieces of equipment, valves, piping, etc., by marking them.  All items of equipment such as fans, pumps, etc., shall be clearly marked using engraved nameplates as hereinafter specified.  The item of equipment shall indicate the same number as shown on the Drawings.  For example, pumps will be identified as 3A, 3B, 3C, etc.; exhaust fans will be E-1, E-2, etc.; supply fans will be S-1, S-2, etc.

Mechanical:

All items of mechanical equipment shall be identified by the attachment of engraved nameplates constructed from laminated phenolic plastic, at least 1/16" thick, 3-ply, with black surfaces and white core.  Engraving shall be condensed Gothic, at least 1/2" high, appropriately spaced.  Nomenclature on the label shall include the name of the item, its mark number, area, space, or equipment served, and other pertinent information.  Equipment to be labeled shall include but not be limited to the following:

NOTE TO SPECIFICATION WRITER:  DELETE ANY INAPPLICABLE EQUIPMENT AND ADD APPLICABLE

ITEMS NOT ALREADY LISTED.

| Pumps | Exhaust Fans |
| --- | --- |
| Fan and Coil Units | Hot Water Generators |
| Condensing Units | Storage Tanks |
| Converters | Compressors |
| Air Conditioning Control | Miscellaneous – similar |
| Panels and Switches | and/or related Items |

Piping:  Pipe markers and arrow markers also shall be provided on but not limited to the piping of the following systems:

NOTE TO SPECIFICATION WRITER:  DELETE ANY INAPPLICABLE ITEMS AND ADD APPLICABLE ITEMS NOT ALREADY LISTED.

| Primary Chilled Water Supply | Steam Condensate |  |
| --- | --- | --- |
| Primary Chilled Water Return | Secondary Chilled Water Supply |  |
| Instrument Air |  |  |
| Atmospheric Relief | Secondary Chilled Water Return |  |
| Low Pressure Steam |  |  |
| Heating Hot Water Supply | Heating Hot Water Return |  |
| Medium Pressure Steam | Acid Waste |  |

Valve Tags:

The Contractor shall provide and install identification tags lettered and numbered to correspond to the information shown on the charts described above.  These tags are to be affixed to all valves except simple service and drain valves located within 10' and within sight of the device or equipment served.  For example, it would not be expected that valves at a pressure reducing station in a machine room would be tagged.  These tags shall be 1/8" thick brass discs, 1 1/2" in diameter.  Each tag shall be attached to its valve with copper clad annealed iron wire or other approved material.

Valves at water headers and steam PRV stations, valves associated with condensate, gas, water meters, and other valves as specified shall also be tagged with standardized color coded plastic tags.  These tags shall be 2 1/2" wide by 1 1/2" high with these color codlings:  Red = normally closed; Green = normally open; Blue = open in winter, closed in summer; and Yellow = closed in winter, open in summer.  Tags should be engraved on both sides.

In addition, pipe runs throughout the building including those above lift out ceilings, under floor, and those exposed to view when access doors or access panels are opened shall be identified by means of Pipe Markers.  Concealed areas, for purposes of this identification section, are those areas which cannot be seen except by demolition of the building elements.  In addition to the pipe markers, arrow markers shall be used to indicate direction of flow.  The following specific instructions shall apply to the application of these markers:

Provide a pipe marker at each valve to indicate proper identification of pipe contents.  Where several valves exist on one header, it is necessary to mark only the header.

Provide an arrow marker with each pipe marker pointing away from the pipe marker to indicate direction of flow.

Provide a double ended arrow marker when flow can be in either or both directions.

Provide a pipe marker and an arrow marker at every point of pipe entry or exit where line goes through a wall or service column.

Provide pipe markers and arrow markers at intervals not exceeding 50 feet and changes in room/space.

Markers shall be located on the two lower quarters of the pipe where view is unobstructed.

Use snap-on type identification for all piping systems, 3/4" thru 6".  For piping systems larger than 6", use strap on markers.

Pipe Markers shall conform to ANSI A 13.1-1981 "Scheme for the Identification of Piping Systems.”  Arrow markers must have same ANSI background colors as their companion pipe markers, or be incorporated into the pipe identification marker.

Locate markers to be visible from floor.

Specials:

Refer to special requirements noted in the various sections hereinafter bound.

EXECUTION

PREPARATION

Degrease and clean surfaces to receive adhesive for identification materials.

Prepare surfaces in accordance with Division 9 for stencil painting.

INSTALLATION

Install plastic nameplates with corrosive-resistant mechanical fasteners, or adhesive.  Apply with sufficient adhesive to ensure permanent adhesion and seal with clear lacquer.

Install tags with corrosion resistant chain. Lead is forbidden.

Apply stencil painting in accordance with Division 9.

Install plastic pipe markers in accordance with manufacturer's instructions.

Install underground plastic pipe markers 6 to 8 inches (150 to 200 mm) below finished grade, directly above buried pipe.

Identify chillers, boilers, air handling units, VAVs, pumps, heat transfer equipment, tanks, and water treatment devices with plastic nameplates. Small devices, such as in-line pumps, may be identified with tags.

Identify control panels and major control components outside panels with plastic nameplates.

Identify thermostats relating to terminal boxes with P-Touch labels.

Identify valves in main and branch piping with tags.

Identify radiator valves with numbered tags.

Tag automatic controls, instruments, and relays.  Key to control schematic.

Provide ceiling tacks to locate valves, dampers or other concealed equipment above T-bar type panel ceilings.  Locate in corner of panel closest to equipment.

END OF SECTION 23 05 53