|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 www.uth.edu |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 23 06 20

HYDRONIC SPECIALTIES

To receive current updates of standard specification Sections, please go to the web site at: http://www.uth.edu or contact the Office of Facilities Planning and Engineering

.

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | October 2022 | 6 | Issuance |

SECTION 23 06 20 – HYDRONIC SPECIALTIES

GENERAL

The following sections are to be included as if written herein:

Section 23 00 00 – Basic Mechanical Requirements

Section 23 05 29 – Sleeves, Flashings, Supports and Anchors

Section 23 05 53 – Mechanical Identification

Section 23 20 00.A – Piping, Valves, and Fittings

WORK INCLUDED

Expansion Tanks

Automatic Air Vents

Air Separators

Strainers

Gauges and Gauge Connections

Thermometer and Thermometer Wells

Pump Suction Fittings

Water Relief Valves

Water Flow Measuring and Balancing System

Chilled Water and Steam Integrating Meters

RELATED WORK

Section 23 21 00 - Hydronic Piping

Section 23 22 00 – Steam and Steam Condensate Piping

REFERENCES

ANSI/ASME - Boilers and Pressure Vessels Code (BPVC)

REGULATORY REQUIREMENTS

Conform to ANSI/ASME Boilers and Pressure Vessels Code Section VIII for manufacture of tanks.

QUALITY ASSURANCE

Manufacturer:  For each product specified, provide components by same manufacturer throughout.

SUBMITTALS

Submit shop drawings and product data under provisions of Section 23 00 00.

Submit shop drawings and product data for manufactured products and assemblies required for this project.

Include component sizes, rough in requirements, service sizes, and finishes.  Include product description, model number and dimensions.

Submit inspection certificates for pressure vessels.

Submit manufacturer's installation instructions under provisions of Section 23 00 00.

OPERATION AND MAINTENANCE DATA

Submit operation and maintenance data under provisions of Section 23 00 00.

Include installation instruction, assembly views, lubrication instructions, and replacement parts list.

DELIVERY, STORAGE, AND HANDLING

Deliver products to site under provisions of Section 23 00 00.

Store and protect products under provisions of Section 23 00 00.

PRODUCTS

EXPANSION TANKS

Construction:  Closed, welded steel, tested and stamped in accordance with Section VIII D of ANSI/ASME BPVC; 125 psi rating; cleaned, prime coated, and supplied with steel support saddles; with tappings for installation of accessories.

Quick Connect Air Inlet: Schrader type valve, manual air vent, tank drain, and pressure relief valve.

Automatic Cold Water Fill Assembly:  Pressure reducing valve, reduced pressure double check back flow preventer, test cocks, strainer, vacuum breaker, and valved bypass.

Hot Water Heating System:  Set expansion tank pressure relief valve at 125 psi maximum and pressure reducing valve at 100 psi.

Chilled Water System:  Set expansion tank pressure relief valve at 125 psi maximum and pressure reducing valve at 100 psi.

Refer to schedule on plans for capacities and dimensions.

AUTOMATIC AIR VENTS

Provide an automatic air vent,at the highest points of the chilled water and hot water systems and on the chilled and hot water coils and elsewhere as shown on the Drawings,  Armstrong No. 21AR or approved equal with a pressure rating of 250 psig.  Provide shut-off valve to facilitate maintenance of air vent.  Locate all air vents and their discharge lines in accessible locations, preferably clustered.

AIR SEPARATORS

Dip Tube Fitting:  For 125 psig operating pressure; to prevent free air collected in boiler from rising into system.

In-line Air Separators:  Cast iron for sizes 1-1/2 inches and smaller, or steel for sizes 2 inches and larger; tested and stamped in accordance with Section VIII D of ANSI/ASME BPVC; for 125 psig operating pressure.

Air Elimination Valve:  Bronze, float operated, for 125 psig operating pressure.

Combination Air Separators/Strainers:  Steel, tested and stamped in accordance with Section VIII D of ANSI/ASME BPVC, for 125 psig operating pressure, with galvanized steel integral strainer with 3/16 inch perforations, tangential inlet and outlet connections, and internal stainless steel air collector tube.

STRAINERS

Each control valve for chilled water and heating water, and each pressure reducing valve assembly regardless of its size shall be preceded by a sediment strainer.  The arrangement of these sediment strainers shall be such that the screens may be removed for cleaning with ease through a gasketed plug.  Monel or stainless steel shall be used to fabricate the noncollapsible lapped screens, which shall contain no soldered joints.

Sediment strainers shall be placed in piping systems wherever shown on the Drawings and at such other points as may be required for the removal of foreign material from the piping systems.

In piping two inches (2") and smaller, strainers shall be Mueller 11M, Watts 77S, or approved equal wye-strainer. Strainers 2-1/2" and larger shall be Mueller 781 series, Watts 77F or approved equal wye-strainer.

Strainers, 2" and smaller shall have a cast steel body, screwed ends, No. 20 mesh strainer, and screwed cap with bronze blow off valve (size to be determined by standard tap size in cap).  Strainers, 2 1/2" and larger shall have a cast steel body, dielectric isolating type flanged ends where installed in copper lines, 0.125” perforated Monel or stainless steel strainer, and flanged cap with bronze ball blow off valve (size of blow off valve shall be determined by standard tap size in cap).  All strainers 6" and larger shall have studs mounted in the body flange in lieu of bolts for removal of cap.  Baskets for strainers 6" and larger shall have stainless steel reinforcing bands at ends to prevent collapsing.

Full sized blow off valves shall be installed on all strainers in steam, condensate, chilled and hot water lines and a drain shall be installed from each valve to the nearest floor drain.

GAUGES AND GAUGE CONNECTIONS

Furnish and install Ashcroft No. 1279A Duragauges on both suction and discharge sides of pumps, complete with Ashcroft No. 1095 lever handle shut-off cocks, and Ashcroft No. 1106B pulsation piston type dampeners, or approved equal. Porous type will not be accepted. Gauges shall have stainless steel movement and be accurate to 0.5%. Gauges shall be in PSI. Gauges shall have back connection when used on a panel; otherwise they shall have bottom connections. The graduation of the dials and the arrangement of the mechanisms shall conform to the pressure range details shown on the Drawings.

Combination pressure or vacuum gauges shall be Ashcroft Duragauges Number 1279A, with an appropriate vacuum range, or approved equal.  The accessories for these gauges shall conform to those prescribed for pressure gauges.

Furnish and install, where noted or indicated on the accompanying Drawings or called for elsewhere in these Specifications, gauge connections complete with Ashcroft No. 1095 lever handle union shutoff cocks, or approved equal.  All gauge connections shall be made up with brass pipe, nipples and brass screw fittings.

THERMOMETER AND THERMOMETER WELLS

Furnish and install thermometers of not less than 9" scale complete with brass separable sockets with extension neck to allow for insulation of piping.  These thermometers shall be red reading tube type with mercury in one piece glass tubes extending from top of scale to sensor, and shall be located so that they may be easily read.  Field adjustable angle thermometers are acceptable.  Thermometers shall in all cases be installed upright or at the proper angle to be read while standing on the floor.  The wells for thermometers shall be located in vertical pipes where possible and when necessary in horizontal pipes they shall be installed in the side and not on the top of the pipe.  They shall be Weksler Industrial Thermometers, or approved equal, with range of 0 to 100 degrees F. for chilled water, and 0 to 220 degrees F for hot water.

Thermometer wells and thermometers shall be located where noted on the accompanying Drawings and where called for in other sections of the Specifications. Thermometer test wells only shall be installed in a vertical position in horizontal lines and at 45 degrees, in vertical lines to hold a fluid in the well.

Thermometer test wells shall be 3/4" Weksler Thermal Wells, brass with stem of minimum length to extend beyond the mid-diameter of the pipe, 2-1/2" extension neck, and brass screw plug.  Wells shall be suitable for use of industrial type thermometers.

Indicating thermometers shall be placed in lines wherever shown on the Drawings.  These thermometers shall be Weksler Industrial Thermometers having stainless steel separable sockets and scales of the range shown on the Drawings.

Provide thermometer and thermowell assemblies, as described above, with one assembly each for the chilled water supply and return main pipes.  Install the assemblies in close proximity to the RTDs that are provided for the chilled water BTU meter.

WATER RELIEF VALVES

The pressure relief valves installed for the protection of the water circulating circuits shall be Bell & Gossett 790 single seated diaphragm and spring type valves with screwed connections or approved equal.  They shall be 3/4" size of bronze construction with EPDM diaphram and seat.

CHILLED [AND HOT] WATER [AND STEAM CONDENSATE] FLOW MEASURING AND BALANCING SYSTEM (SUB-METERING)

Furnish and install complete Onicron System 10 BTU metering system.

This shall be a coordinated system. Flow Stations shall be Onicron F-3000 series or approved equal inline electromagnetic flow meters. Flow Station shall be installed in a straight run of pipe in accordance with manufacturer's requirements for the specific installation in order to maintain rated accuracy.

Unit shall accommodate the following fluid operating ranges:

Temperature: 36° to 250° F.

Pressure:     0 to 150 psi.

BUILDING MAIN CHILLED [AND HOT] WATER [AND STEAM CONDENSATE] INTEGRATING METERS:

Furnish and install complete Onicron System 10 BTU metering system.

This shall be a coordinated system. Flow Stations shall be Onicron F-3000 series inline electromagnetic flow meters. Flow Station shall be installed in a straight run of pipe in accordance to manufacturer's guidance for the specific installation in order to maintain rated accuracy.  Flow stations shall be of steel construction, welded in place.

Each flow station shall consist of a flow sensor with laminated or metal identification tag on chain giving pipe size, meter series, and station identification.

Wall mounted meter shall be complete with adequate lengths of cables to attached sensors, and installation and operating instructions.  Meter shall operate on 115 VAC. Meter shall be backlit LCD and shall indicate:

Instantaneous flow rate in GPM, and total flow in gallons.

Meter shall have dual outputs for each of the displayed values.  Out puts shall be 4-20 mA and TTL pulse rate, each proportional to display values, compatible with building EMS.

Meter shall have positive zero flow indication.

Unit shall accommodate the following fluid operating ranges:

Temperature: 36° to 250° F.

Pressure:     0 to 150 psi.

NOTE TO SPECIFICATION WRITER:  IN CASE ORIFICE IS PROVIDED WITH CDAS, PROVIDE STEAM FLOW METER MANUFACTURER WITH ORIFICE DATA.  STEAM FLOW METER MANUFACTURER NEEDS TO KNOW ORIFICE DIFFERENTIAL REQUIREMENTS FOR PROPER RANGE SELECTION.  STEAM FLOW METER MANUFACTURER WILL NEED TO KNOW IF HE IS TO PROVIDE ORIFICE AND ORIFICE FLANGES.

EXECUTION

INSTALLATION AND APPLICATION

Install specialties in accordance with manufacturer's instructions to permit intended performance.

Support tanks inside building from building structure in accordance with manufacturer's instructions.

Provide manual air vents at system high points and as indicated.

Provide manual air vents at entrance to all heating hot water coils, with a "cane" shaped discharge tube, positioned to permit draining to a portable receptacle.

For automatic air vents in ceiling spaces or other concealed locations, extend vent tubing to nearest drain.

Provide air separator on suction side of system circulation pump and connect to expansion tank.

Provide valved drain and hose connection on strainer blow down connection.

Provide pump suction fitting on suction side of base mounted centrifugal pumps.  Remove temporary strainers after cleaning systems.  Clean all permanent strainers after circulating systems for a minimum of 48 hours at full capacity.

Support pump fittings with floor mounted pipe and flange supports.

Provide relief valves on pressure tanks, low pressure side of reducing valves, heat exchangers, and expansion tanks.

Select system relief valve capacity so that it is greater than make-up pressure reducing valve capacity.  Select equipment relief valve capacity to exceed rating of connected equipment.

Pipe relief valve outlet to nearest floor drain.

Where one line vents several relief valves, make cross sectional area equal to sum of individual vent areas.

Provide pipe unions and  isolation valves in pipe, on both sides of air handler control valves to facilitate change out of valve.

END OF SECTION 23 06 20.13