|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 WWW.UTH.EDU |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 23 07 16

EQUIPMENT INSULATION

To receive current updates of standard specification Sections, please go to the web site at: http://www.uth.edu or contact the Office of Facilities Planning and Engineering

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | October 2022 | 6 | Issuance |

SECTION 23 07 16 – EQUIPMENT INSULATION

GENERAL

The following sections are to be included as if written herein:

Section 23 00 00 – Basic Mechanical Requirements

Section 23 05 29 – Sleeves, Flashings, Supports and Anchors

Section 23 05 53 – Mechanical Identification

SECTION INCLUDES

Equipment insulation

Covering

Breaching insulation

RELATED SECTIONS

Section 09 91 00 - Painting: Painting insulation covering

REFERENCES

ASTM B209 – Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

ASTM C177 – Standard Test Method for Steady-State Heat Flux Measurements and Thermal Transmission Properties by Means of the Guarded- Hot-Plate Apparatus

ASTM C195 – Standard Specification for Mineral Fiber Thermal Insulation Cement

ASTM C335 – Standard Test Method for Steady-State Heat Transfer Properties of Pipe Insulation

ASTM C449 – Standard Specification for Mineral Fiber Hydraulic-Setting Thermal Insulating and Finishing Cement

ASTM C518 – Standard Test Method for Steady-State Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus

ASTM C533 – Standard Specification for Calcium Silicate Block and Pipe Thermal Insulation

ASTM C534 – Standard Specification for Preformed Flexible Elastomeric Cellular Thermal Insulation in Sheet and Tubular Form

ASTM C552 – Standard Specification for Cellular Glass Thermal Insulation

ASTM C553 – Standard Specification for Mineral Fiber Blanket Thermal Insulation for Commercial and Industrial Applications

ASTM C612 – Standard Specification for Mineral Fiber Block and Board Thermal Insulation

ASTM C921 – Standard Practice for Determining the Properties of Jacketing Materials for Thermal Insulation

ASTM D1056 – Standard Specification for Flexible Cellular Materials - Sponge or Expanded Rubber

ASTM E84 – Standard Test Method for Surface Burning Characteristics of Building Materials

ASTM E96 – Standard Test Methods for Water Vapor Transmission of Materials

ASTM E84 – Standard Test Method for Surface Burning Characteristics of Building Materials

UL 723 – Test for Surface Burning Characteristics of Building Materials

SUBMITTALS

Submit under provisions of Section 23 00 00.

Product Data:  Provide product description, list of materials and thickness for equipment scheduled.

Samples:  Submit two samples of any representative size illustrating each insulation type.

Manufacturer's Installation Instructions:  Indicate procedures which ensure acceptable workmanship and installation standards will be achieved.

QUALITY ASSURANCE

Materials: Flame spread/smoke developed rating of 25/50 in accordance with UL 723/ASTM E84.

QUALIFICATIONS

Applicator:  Company specializing in performing the work of this section with minimum three years experience.

DELIVERY, STORAGE, AND HANDLING

Deliver, store, protect and handle products to site under provisions of Section 23 00 00.

Deliver materials to site in original factory packaging, labeled with manufacturer's density and thickness.

Store insulation in original wrapping and protect from weather and construction traffic.

Protect insulation against dirt, water, chemical, and mechanical damage.

ENVIRONMENTAL REQUIREMENTS

Maintain ambient temperatures and conditions required by manufacturers of adhesives, mastics, and insulation cements.

Maintain temperature during and after installation for minimum period of 24 hours.

PRODUCTS

General

Unless otherwise noted, equipment shall be insulated with same insulation type and thickness as is used for piping which equipment serves.

Type a: high temperature fiberglass

ESLIN EG-SCUI or equal glass fiber insulation piping insulation with a “K” factor of 0.30 BTU-In/Hr.-degree F at 200°F and 0.48 BTU-In/Hr.-degree F at 600°.

Rated maximum service temperature of 1200°F (650°C).

Maximum density of 12.5 lbs/ft³

Compressive strength of 28.5 psi minimum when tested in accordance with ASTM C165.

Rated as 0 flame spread and 0 smoke developed when tested in accordance with ASTM E84, UL 723, CAN/ULC-S102-M88 or NFPA 255.

Certified to meet the requirements of ASTM C795 for use over stainless steel.

Rated as noncombustible when tested in accordance with ASTM E136.

Insulation treated with water resistant resin on the surface and within each layer of the insulation

Thickness of insulation shall be sufficient to reduce the surface temperature to the maximum permitted by OSHA and other governing criteria, but in no case more than 150 degrees F.

type B: Foam Glas

Foamglas One Insulation with a “K” factor of 0.29 BTU-In/Hr.-degree F at 75°F manufactured by Pittsburgh Corning Corporation and fabricated by a Pittsburgh Corning Corporation-approved fabricator. Water vapor permeability shall be 0.00 perm-in. The insulation shall comply with ASTM C 552 Type II, furnished in half sections up to 36 inches long or segments 18 inches long.

        - Rated maximum service temperature of 900°F.

        - Maximum density of 7.3 lbs/ft³

        - Compressive strength of 90 psi minimum when tested in accordance with ASTM C165.

        - Rated as 0 flame spread and 0 smoke developed when tested in accordance with ASTM E84, UL 723, CAN/ULC-S102-M88 or NFPA 255.

        - Certified to meet the requirements of ASTM C795 for use over stainless steel.

        - Rated as noncombustible when tested in accordance with ASTM E136.

        - Fitting insulation shall be applied in same manner as pipe application.  Refer to piping insulation specification for proper guidance.

PUMPS:

Each water pump shall not be insulated but the insulation of the connecting piping shall be continued up to the face of the flanges on the piping connection to the pump and any bare metal that projects over the bed plate of the pump and from which condensation might drip onto the floor.

The heating hot water pump and the condensate return pump shall not be insulated but the insulation of the connecting piping shall be beveled to the face of the pipe flange connection to the pump flange.

BUILT UP AIR CONDITIONING CASINGS AND DRAIN PANS:

All walls and ceilings in the built up system plenums shall be lined with Micro-Aire M/F Fiberglass ductboard Type 475, 1" thick.  Liner shall be applied to the ceilings and walls with quick tacking rubber base adhesive.  Liner shall be additionally secured to surfaces with stick clips and washers spaced 16" on centers.  Provide No. 6 mountings, ASTM-C-60T sound absorption test method.

Floors of built up system plenums shall be insulated externally (beneath the floor surface) with 2 inch thick Insulation A, or its equivalent (including vapor barrier protection) integrated into the architectural/structural construction, in all instances where plenums may act as drain pans or otherwise collect moisture, or where personnel access is possible.  In all other plenums, floors shall be lined as hereinbefore specified for walls and ceilings.

Protective jacketing

Metal jacketing: Aluminum or stainless steel jacket, 0.016” thick, banded with ¾” aluminum banding (0.020” thick) using 3 bands per three foot (3’) section of covering.

EXECUTION

EXAMINATION

Verify that equipment has been tested before applying insulation materials.

Verify that surfaces are clean, foreign material removed, and dry.

INSTALLATION

Install materials in accordance with manufacturer's instructions.

Do not insulate factory insulated equipment.

On exposed equipment, locate insulation and cover seams in least visible locations.

Apply insulation close to equipment by grooving, scoring, and beveling insulation.  Secure insulation to equipment with studs, pins, clips, adhesive, wires, or bands.

Fill joints, cracks, seams, and depressions with bedding compound to form smooth surface.  On cold equipment, use vapor barrier cement.

Insulated dual temperature equipment or cold equipment containing fluids below ambient temperature:

Provide vapor barrier jackets, factory applied or field applied.

Finish with glass cloth and vapor barrier adhesive.

Insulate entire system.

For insulated equipment containing fluids above ambient temperature:

The use of asphaltic compounds in higher-than-ambient temperature service is prohibited.

Provide standard jackets, with or without vapor barrier, factory applied or field applied.

Finish with glass cloth and adhesive.

For hot equipment containing fluids 140 degrees F or less, do not insulate flanges and unions, but bevel and seal ends of insulation.

For hot piping conveying fluids over 140 degrees F, insulate flanges and unions, including those at equipment, but label the insulation to indicate a concealed flange or union.

Inserts and Shields:

Application:  Equipment 2 inches diameter or larger.

Shields:  Galvanized steel between hangers and inserts.

Insert location:  Between support shield and equipment and under the finish jacket.

Insert configuration:  Minimum 6 inches (150 mm) long, of same thickness and contour as adjoining insulation; may be factory fabricated.

Insert material:  Heavy density insulating material suitable for the planned temperature range.

Finish insulation at supports, protrusions, and interruptions.

For equipment in mechanical equipment rooms or in finished spaces, finish with aluminum jacket.

For exterior applications, provide vapor barrier jacket or finish with glass mesh reinforced vapor barrier cement.  Cover with aluminum jacket with seams located on bottom side of horizontal equipment.

Cover cellular glass and cellular foam insulation with aluminum jacket.

Do not insulate over any nameplate or ASME stamps.  Bevel and seal insulation around such.

Install insulation for equipment requiring access for maintenance, repair, or cleaning, in such a manner that it can be easily removed and replaced without damage.

All piping, equipment, ductwork, all plenums including metal and masonry construction, fans, etc., shall be insulated as indicated on the Drawings, as specified herein, and as required for a complete system.  In each case, the insulation shall be equal to that specified and materials applied and finished as described in these Specifications.

All insulation shall be applied by mechanics skilled in this particular work and regularly engaged in such occupation.  All insulation shall be applied in strict accordance with these Specifications and with factory printed recommendations on items not herein mentioned.  Unsightly, inadequate, or sloppy work will not be acceptable, and all such work shall be removed and replaced as many times as necessary to achieve an acceptable installation.

All insulation, jacket, adhesives, mastics, sealers, etc., utilized in the fabrication of these systems shall meet NFPA for fire resistant ratings (maximum of 25 flame spread and 50 smoke developed ratings) and shall be approved by the insulation manufacturer for guaranteed performances when incorporated into their insulation system, unless a specific product is specified for a specific application, and is stated as an exception to this requirement.  Certificates to this effect shall be submitted along with Contractor's submittal data for this section of the Specifications.  No material may be used that, when tested by the ASTM E84-89 test method, is found to melt, drip or delaminate to such a degree that the continuity of the flame front is destroyed, thereby resulting in an artificially low flame spread rating.

All surfaces to be insulated shall be clean and dry before applying the insulation.  All sections of molded pipe covering shall be firmly butted together.  Where an insulation covering is applied, it shall lap the adjoining section of insulation by at least three inches (3").  Where insulation terminates, it shall be neatly beveled and finished.  No insulation shall be applied until the pipe, duct, etc., have been pressure tested and found tight.  Piping, flexible connections, flanges, valves, strainers, and unions shall be covered unless specifically noted otherwise.  Flexible connections on duct shall not be covered.  All materials used shall be fire retardant or nonflammable.  Refer to Section 15A.

Where vapor barriers are required, the vapor barrier shall be on the outside.  Extreme care shall be taken that the vapor barrier is unbroken.  Joints, etc., shall all be sealed.  Where insulation with a vapor barrier terminates, it shall be sealed off with the vapor barrier being continuous to the surface being insulated.  Ends shall not be left raw.

The handling and installation of all insulation materials shall be performed in strict accordance with the manufacturer’s recommendations.

Insulation Application Schedule

| Equipment Type | Service Temperature | Insulation Type | Insulation Thickness | Jacket |
| --- | --- | --- | --- | --- |
| Emergency generator exhaust and piping | 1200 degrees F | Type A | 2” | Metal jacketing |
| Heat exchangers and hot water generators | 75-180 degrees F | Type B | 2” | Metal jacketing |
| Heat exchangers and hot water generators | 181-300 degrees F | Type B | 2 ½” | Metal jacketing |
| Heat exchangers and hot water generators | >300 degrees F | Type B | 3” | Metal jacketing |
| Pumps |  | Per section 2.4 above |  |  |

END OF SECTION 23 07 16