|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 www.uth.edu |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 23 36 00

AIR TERMINAL UNITS (VAV)

To receive current updates of standard specification Sections, please go to the web site at: http://www.uth.edu or contact the Office of Facilities Planning and Engineering

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | October 2022 | 8 | Issuance |

SECTION 23 36 00 – AIR TERMINAL UNITS (VAV)

GENERAL

The following sections are to be included as if written herein:

23 00 00 -- Basic Mechanical Requirements

23 05 29 -- Sleeves, Flashings, Supports and Anchors

23 05 53 -- Mechanical Identification

SECTION INCLUDES

Constant Volume Terminal Units

Variable Volume Terminal Units

Dual Duct Terminal Units

Single Duct Terminal Units

Integral Sound Attenuator

Integral Heating Coils

Integral Damper Motor Operators

Integral Controls

PRODUCTS FURNISHED BUT NOT INSTALLED UNDER THIS SECTION

Section 23 09 00 - Controls and Instrumentation:  Thermostats and Control Components

Section 23 05 93.A - Testing, Adjusting and Balancing

Section 26 05 19 - Cable, Wire and Connectors, 600 Volt

Section 26 27 26 - Wiring Devices and Floor Boxes

RELATED SECTIONS

Section 23 05 13 - Motors

Section 23 21 00 - Hydronic Piping:  Connections to Heating Coils

Section 23 06 20.13 - Hydronic Specialties:  Connections to Heating Coils

Section 23 31 00 - Ductwork

Section 23 33 00 - Ductwork Accessories

Section 23 37 00 - Air Outlets and Inlets

Section 23 09 00 - Controls and Instrumentation

Section 23 05 93.A - Testing, Adjusting and Balancing

Section 26 05 19 - Cable, Wire and Connectors, 600 Volt

Section 26 27 26 - Wiring Devices and Floor Boxes

REFERENCES

NFPA 90A - Installation of Air Conditioning and Ventilation Systems

UL 181 - Factory-Made Air Ducts and Connectors

ADC 1062 - Air Distribution and Control Device Test Code

ARI 880 - Standard for Air Terminals

SUBMITTALS

Submit shop drawings under provisions of Section 23 00 00.

Submit shop drawings indicating configuration, general assembly, and materials used in fabrication.

Submit product data indicating configuration, general assembly, and materials used in fabrication.  Include catalog performance ratings which indicate airflow, static pressure, and NC designation.

Include schedules listing discharge and radiated sound power level for each of second through seventh octave bands at inlet static pressures of one inch wg, submit minimum air flow for heating coil operation and minimum airflow for flow measurement within specified accuracy

Submit Manufacturer's installation instructions under provisions of Section 23 00 00.

A sample 8-inch size production run unit shall be submitted for examination and approval by the Engineer, RCM office and the Owner’s Testing and Balancing (TAB) Consultant.  This submittal box shall be submitted, in addition to the required written submittal, well in advance of any requirement for installation  of boxes, but absolutely no later than 60 days after the date of the start of construction stipulated in the Work Order letter from the Owner to the General Contractor.  A minimum of three weeks shall be allowed by the Contractor for the testing of the box from the time of submittal to the time of determination of project worthiness.  This period shall restart if the sample box is rejected and another box is resubmitted.  If rejected for any reason, the Contractor shall expedite the corrections documented, and shall resubmit a sample box as soon as possible.  Any delay in the submittal of the box for approval shall not be grounds for a claim of delay on the part of the Contractor.  If approved, the unit shall remain in the possession of the Owner at the job site for comparison with units as shipped to project.  The unit shall be installed in the project, at an accessible, marked location.  The unit Manufacturer shall test and certify that each box used on this project has been tested as specified.

OPERATION AND MAINTENANCE DATA

Submit operation and maintenance data under provisions of Section 23 00 00.

Include Manufacturer's descriptive literature, operating instructions, maintenance and repair data, and parts lists.

QUALIFICATIONS

Manufacturer:  Company specializing in manufacturing the products specified in this section with minimum three years’ documented experience.

WARRANTY

Provide one-year Manufacturer's warranty under provisions of Section 23 00 00.

PRODUCTS

VARIABLE OR CONSTANT VOLUME TERMINAL UNITS:

The Contractor shall provide pressure independent dual duct or single duct (as scheduled) variable air volume control assemblies with integral attenuator (single duct units) and attenuator/mixers (dual duct units) of the sizes, capacities, and configurations shown on the drawings.

CASING CONSTRUCTION:

The units shall be constructed of a minimum of 22-gauge galvanized steel and internally lined with a minimum of 1 inch thick, three pound per cubic foot density insulation.  The insulation shall be foil faced with the edges and seams sealed or "captured", encapsulating all fibers of the insulation.  The insulation shall be neatly installed with no rough edges to interrupt the smooth flow of air through the box.  Closed cell polymer insulation may be used instead of the fiberglass described above if UL 25/50 labeled.  The casing shall be insulated throughout its interior, up to or at least to within 2" of the heating coil connection.  Insulation for the heating coil shall enclose the coil casing and tube bends and shall overlap the box internal lining by at least 3".  The external insulation shall be as specified in other sections of this specification for duct insulation with full vapor barrier, and shall be field installed unless coil and plenum section is furnished as an integral part of the box.

All interior features of the boxes (such as mixing baffles, damper housings, etc.) shall be secured within the casing to avoid excessive movement or rattling with air movement or externally generated vibration.  All external features of the terminal units shall be designed not to extend beyond the ends of the unit.  (For example, the actuator mounting brackets, etc. shall not extend beyond the plane of the inlet "bulkhead.")  The only exception shall be flow sensors installed in the inlet duct connections.  Note that if a separate flow station is installed within a frame within the casing, then it shall be so installed not to allow airflow to bypass the flow measurement station.

No portion of the VAV terminal shall block access to the flow ring connections on the unit inlets.  Note that this will require some manufacturers to mount their control panels further forward than their standard construction.

The terminal units shall be constructed with inlet and discharge ductwork connections.  The inlet ductwork connections shall extend a minimum of 4 inches from the unit casing including an allowance for the installation of airflow station(s) or probe(s).  The discharge connection shall include 1" extension with slip and drive connections for use by the Contractor to secure the discharge ductwork or appurtenances to the unit and shall be reinforced to provide a rigid assembly.

CASING LEAKAGE:  Assembled units shall be so constructed and sealed to limit air leakage to the following listed quantities at 6" static pressure.  If sealing is required to obtain the leakage performance, seal as for medium pressure ductwork Hardcast 1602 tape may be used to seal lap joints and flat seams only.  Leakage curves or tables will be required as part of the submittal data.  The following is the maximum allowable casing leakage including all components:

| Diameter | Maximum CFM (@ 2000 fpm inlet velocity) | Maximum Allowable CFM Casing Leakage |
| --- | --- | --- |
| 4"-5"-6" | 395 | 8.0 |
| 7"-8" | 700 | 14.0 |
| 9"-10" | 1090 | 22.0 |
| 11"-12" | 1570 | 30.0 |
| 13"-14" | 2140 | 40.0 |

ACCESS PLENUM AND DOOR:  Single duct units provided with reheat coils also shall be provided with an access section or plenum between the terminal and the coil for coil inspection.  The construction of the plenum shall be equal to the quality of materials and workmanship to that of the terminal unit.  The access plenum may also be used as a transition, and shall be constructed with a transition angle not to exceed 15 degrees.  The access plenum shall contain a minimum of a 12 inch diameter or 12 inch by 12 inch (or full width of unit if less than 12") access door. Door shall be Ventlok Galvanized Sheet Metal Access Door, Flexmaster Inspector Series, Ward DSP or DSA series, or equal.  Door frame may be bolted, screwed or flanged and sealed to the casing.  Door shall be gasketed and shall be double wall construction or insulated similar to main casing.  Door shall be held in place with latches or other captive retainer devices.  An additional access panel shall be provided immediately downstream of the dampers for inspection and service of the dampers.  If the damper assembly is easily removed from the rear of the box, the access size can be reduced to 8" round or 8" x 8" for inspection only.

Access doors and frames shall be thermally broken

DAMPER CONSTRUCTION:  The damper blades shall be an equivalent of 18-gauge galvanized steel or equal aluminum and shall be securely riveted or bolted through the damper shafts to assure no slippage of the blades.  The damper shafts shall operate in rust-proof self-lubricating bearings.  Damper shafts penetrating the unit casings shall be sealed against leakage, and bearings shall be installed for protection against wear in the casing penetration.  Damper shafts shall be formed of, or cut from solid stock; no hollow shafts will be allowed.  The dampers shall seat against gasketed stops or the dampers shall have gasketed edges. Gaskets shall be mechanically fastened to the blades. If the fastening method is not full contact clamping type, then the addition of adhesive to the gasket shall be required. The dampers shall be so constructed to prevent "oil canning" of the damper blade.  The units shall be tested for leakage in both inlets with 6" static pressure imposed on one inlet at a time.  The maximum percent leakage from all tests shall be reported.  Leakage curves as a function of pressure shall be supplied as part of the submittal data.  The damper actuator linkage, if used, shall be constructed of material of sufficient strength to avoid buckling under extreme loads.  Also, linkages shall not allow play greater than 5 degrees of damper movement.  The controls for the dampers shall cause the dampers to fail in the position of last control (freeze in place), or fail to the open position.

DAMPER LEAKAGE:  The following is the maximum damper leakage allowable for the various size diameter inlets at 6" wg differential pressure.  The damper leakage shall not exceed the values listed in the table below at 6" S.P., following ARI 880 Testing Procedures.

| Diameter | Maximum CFM (@ 2000 fpm inlet velocity) | Maximum Allowable CFM Damper Leakage |
| --- | --- | --- |
| 4"-5"-6" | 395 | 6 |
| 7"-8" | 700 | 10.5 |
| 9"-10" | 1090 | 16.5 |
| 11"-12" | 1570 | 20 |
| 13"-14" | 2140 | 30 |

NOTE TO SPECIFYING ENGINEER: NOTE BOXES WHICH WILL EXCEED PRESSURE DROP LISTED IN THE FOLLOWING PARAGRAPH SPECIFICALLY ON THE SCHEDULE AND INCLUDE SENTENCE REFERING TO SCHEDULE. CONFIRM BOX ACCEPTABILITY WITH OWNER/PROJECT MANAGER.

UNIT PRESSURE DROP:  For dual duct units with an integral attenuator-mixer, but with no other accessories, the static pressure across the assembly with an equivalent 2000 fpm inlet velocity through one inlet shall not exceed 0.5 inches water gauge, with the total flow through either inlet.  Single duct unit pressure drop shall be limited to 0.40 inches water gauge under the same conditions above [unless otherwise specifically noted on terminal box schedule]. Units with hot water reheat coils shall have a water side pressure drop of no more than 10 ft of head at the schedule flow.

CERTIFICATION:  The Unit Manufacturer shall certify that each unit used on this project will perform as specified.  Each unit shall bear a tag or decal listing the following specified information:

Test Pressure

Leakage CFM (damper)

Leakage CFM (casing)

Date of Mfg.

Room or area served

Unit size - 6”, 8”, etc.

Calibrated CFM, i.e. 800 CFM

MIXING:  Terminal units as specified herein shall provide mixing within the units, and not rely upon the discharge ductwork to provide for the completion of the mixing process.  The horizontal average temperature of the air as it leaves the terminal unit shall not vary more than 1°F for each 20°F. of temperature difference between the two inlet air supplies.  (For example, if the cold supply air is 55°F. and the hot supply air is 95°F., the difference is 40 degrees.  The allowable temperature variation of the discharge air is, thus, 2°F.)  The temperature of the discharge air shall be measured using a pattern of four vertical, evenly spaced columns, and three horizontal, evenly spaced rows.  The rows and columns shall be spaced so that the resulting 12 points shall be at the centers of equal areas.  The plane of the points shall be perpendicular to the direction of airflow, within 4 inches of the discharge of the terminal unit, within the discharge ductwork.  The three readings in each column shall be averaged to determine compliance with the 1° criteria.

FLOW MEASUREMENT:

Airflow measurement systems shall measure airflow through the inlet connections with 5% of actual airflow between 2000 fpm and 250 fpm with three straight duct diameters on each air inlet connection.

Where flow measurement is indicated to be on the discharge side of the air terminal, the manufacturer is responsible for locating the flow measurement device so that it meets the accuracy requirements above from the minimum to the maximum settings for the box and each deck connection.  As a substitute, the manufacturer and contractor may elect to provide an external flow measure device and required duct modifications at no additional cost to the owner.

SOUND:  (Note that the maximum sound levels listed in this paragraph refer to raw sound levels, with no credits taken for the construction.)

DISCHARGE SOUND

Maximum discharge Sound Power Levels at 2000 fpm primary air inlet velocity with 1.5 inch wg inlet static pressure shall not exceed that listed in the following table.  No credit for lined discharge duct, branching, flow division, end reflection, room absorption or any other effects shall be allowed.

| - Octave Band | - Center Frequency - (Hz) | - Sound Power Level - (dB re 10-12 Watts) |
| --- | --- | --- |
| - 2 | - 125 | - 76 |
| - 3 | - 250 | - 66 |
| - 4 | - 500 | - 63 |
| - 5 | - 1000 | - 58 |
| - 6 | - 2000 | - 60 |
| - 7 | - 4000 | - 55 |

RADIATED SOUND

Maximum discharge Sound Power Levels at 2000 fpm primary air inlet velocity with 1.5 inch wg inlet static pressure shall not exceed that listed in the following table.  No credit for ceiling plenum, ceiling tiles, room absorption, or any other effects shall be allowed.

| - Octave Band | - Center Frequency - (Hz) | - Sound Power Level - (dB re 10-12 Watts) |
| --- | --- | --- |
| - 2 | - 125 | - 72 |
| - 3 | - 250 | - 67 |
| - 4 | - 500 | - 64 |
| - 5 | - 1000 | - 54 |
| - 6 | - 2000 | - 47 |
| - 7 | - 4000 | - 45 |

All sound power levels shall be obtained from testing in accordance with ARI-ADC Standard 880 and shall be certified at ARI-880 certification points.

TESTING PRIOR TO INSTALLATION:

Refer to Submittal Paragraph, this section, for sample unit testing prior to shipment.

SHIPMENT TESTING:  A minimum of ten percent (10%) of each size of the terminal units (but no less than one unit of each size used) may be tested for conformance to this specification, at the Owner's discretion.  The Contractor shall allow sufficient time during construction and space for the Owner’s TAB Consultant to perform all testing as may be required.

UNIT NON-PERFORMANCE:

If the results of the SHIPMENT TESTING show that any of the units do not perform as specified, then an additional ten percent (10%) of each size (but no less than one unit of a size, unless 100% of the size has been tested) of the units shall be tested.  If this testing, in the Owner’s opinion, shows that ten percent (10%) or more of the units tested do not perform as specified, then one hundred percent (100%) of all sizes of the units shall be tested for conformance with these specifications.  The results of that testing shall be reviewed carefully between the Contractor, Manufacturer, the Owner’s construction administrator(s), and the Owner’s design engineer(s).  A method of repair or replacing the units will be negotiated.  The Owner, however, shall maintain the right of final approval of any proposed solution.

Should for any reason the testing described above under "SUBMITTAL" and "SHIPMENT TESTING" prove that any of the units do not perform as specified, the Contractor shall be responsible for all subsequent labor, travel, travel expenses, and incidental expenses, penalties, or other costs attendant to any additional testing as described under "UNIT NON-PERFORMANCE", or as required to prove that the units perform as specified.  This shall include, but not be limited to, the labor, travel and reasonable incidental expenses of not only the Contractor and Owner’s TAB Consultant, but also those incurred by the Owner as may be specifically required for this purpose.  The expenses to be reimbursed to the Owner shall be labor at a rate of $300 per day or any portion of a day, plus travel and travel expenses at actual cost, plus reasonable incidental expenses at actual cost.

MANUFACTURER:  All Terminal Units shall be as manufactured by Titus (Model MDV-3100-UT or MDC-3100-UT), Metal*Aire (Series TH500-ECO or Series 400DDUT), or Nailor Industries (3000-UT or 3200-UT), or Price Industries.  Note that the model and series numbers listed may differ slightly from catalogue information.  No other Manufacturers or models are acceptable.  Even though specific Manufacturers may be named herein, the material supplied by any approved Manufacturer shall meet all of the provisions of this specification without exception.

Single duct boxes (where specified) shall be the single duct version of the dual duct versions described in the paragraph above.

GENERAL PERFORMANCE:  If DDC controls of another Manufacturer (NOT the terminal unit Manufacturer) are provided for this project, the terminal unit Manufacturer shall be responsible only for the construction of the terminal unit and the installation of internal control components installed at the Manufacturer’s factory, and shall not be responsible for the installation of controls not installed at the terminal unit Manufacturer’s factory, nor shall the Manufacturer be responsible for the performance of the DDC controls.  The performance of DDC controls, especially in connection with terminal units, shall be the responsibility of the DDC controls Manufacturer.

HOT WATER COILS:  Hot water coils installed in conjunction with single duct terminal units shall be factory installed, one or two row with a maximum of 10 aluminum fins per inch.  Air side pressure drop shall be limited to 0.25" wg at box rated cold airflow.  Full fin collars shall be provided for accurate fin spacing and maximum fin-to-tube contact.  Tubes shall be 1/2 inch diameter seamless copper with a minimum wall thickness of 0.016 inch, tested at 300 psig air pressure under water with a minimum rated burst pressure of 1500 psig.  Male sweat-type water connections shall be provided.  Side and end plates shall be a minimum of 18-gauge galvanized sheet metal construction.  All coils shall be constructed and tested in accordance with UL and/or ARI Standards.  The tube ends shall be protected with tube end caps of sheet metal similar to the casing material, and shall be insulated within the caps.

CONTROL PERFORMANCE:  Assemblies shall be able to be reset to any airflow between zero and the maximum cfm shown on Drawings.  To allow for maximum flexibility and future changes, it shall be necessary to make only simple screwdriver or keyboard adjustments to arrange each unit for any maximum airflow within the ranges for each inlet size as scheduled on the Drawings.  The control devices shall be designed to maintain the desired flow regardless of inlet flow deflection.

CONTROL SEQUENCES: Refer to the controls drawings and specifications for sequences of operations for the VAV terminals.

DDC SYSTEMS:

Electronic motors and controllers shall be installed by the terminal unit Manufacturer unless specifically prohibited by the by the controls Manufacturer.  In such an event, the controls Manufacturer shall be responsible for the installation of the controls.  The controls Manufacturer shall be responsible for the operational performance of the entire system.  The terminal unit Manufacturer shall remain responsible only for the performance of the mechanical components of the unit.

DDC Controls Protocol/Description:

NOTE TO SPECIFICATION WRITER: INSERT THE APPROPRIATE DDC CONTROLS PROTOCOL/DESCRIPTION HERE.

EXECUTION

INSTALLATION

Refer also to requirements included in Part 2 of this specification.

Install in accordance with Manufacturer's instructions.

Provide ceiling access doors or locate units above easily removable ceiling components.

Support units individually from structure.  Do not support from adjacent ductwork.

Connect to ductwork in accordance with Section 23 31 00.

Install heating coils in accordance with Section 23 82 16.

All terminal units shall be installed with a minimum of three diameters of straight duct directly prior to the entry into each terminal unit connection and of the same size as the box inlet neck connection.

END OF SECTION 23 36 00