|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 www.uth.edu |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 23 81 23

COMPUTER ROOM AIR CONDITIONING UNITS

To receive current updates of standard specification Sections, please go to the web site at: http://www.uth.edu or contact the Office of Facilities Planning and Engineering

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | October 2022 | 7 | Issuance |

SECTION 23 81 23 – COMPUTER ROOM AIR CONDITIONING UNITS

GENERAL

THE FOLLOWING SECTIONS ARE TO BE INCLUDED AS IF WRITTEN HEREIN:

Section 23 00 00 – Basic Mechanical Requirements

Section 23 05 29 – Sleeves, Flashings, Supports and Anchors

Section 23 05 53 – Mechanical Identification

Section includes

Floor-mounted computer-room air conditioners, 6 tons and larger

Floor-mounted computer-room air conditioners, 5 tons and smaller

Water-cooled computer room air conditioners

PRODUCTS FURNISHED BUT NOT INSTALLED UNDER THIS SECTION

Section 23 09 23 - Controls and Instrumentation: Installation and wiring of thermostats and control components

Section 26 05 19 - Cable, Wire and Connectors, 600 Volt:  Electrical characteristics, cable, wire, materials

Section 26 27 26 - Wiring Devices and Floor Boxes:  Wiring connections

RELATED SECTIONS

Section 09 69 00 - Access Flooring

Section 23 05 13 - Motors:  Evaporator and condenser fan motors

Section 23 07 13 - Ductwork Insulation:  Duct liner

Section 23 09 23 - Controls and Instrumentation

Section 23 20 00 - HVAC Pumps

Section 23 82 16 – Air Coils

REFERENCES

ANSI/ASME - Boilers and Pressure Vessels Code (BPVC)

ANSI/NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum)

ANSI/NFPA 90A - Installation of Air Conditioning and Ventilation Systems

ASHRAE 52 - Air-Cleaning Devices Used in General Ventilation for Removing Particulate Matter

UL - Underwriters Laboratories

REGULATORY REQUIREMENTS

Conform to NFPA 90A for the installation of computer room air conditioning units.

SUBMITTALS

Submit shop drawings and product data under provisions of Section 23 00 00.

Submit shop drawings and product data for manufactured products and assemblies required for this project.

Indicate water, drain, electrical, and refrigeration rough-in connections on shop drawings or product data.

Shop Drawings:  For computer-room air conditioners.  Include plans, elevations, sections, details, and attachments to other work.

Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Wiring Diagrams:  For power, signal, and control wiring.

Submit manufacturer's installation instructions under provisions of Section 23 00 00.

OPERATION AND MAINTENANCE DATA

Submit operation and maintenance data under provisions of Section 23 00 00.

Include manufacturer's descriptive literature, operating instructions, installation instructions, and maintenance and repair data.

WARRANTY

Provide ten-year manufacturer's warranty under provisions of Section 23 00 00.

Warranty:  Include coverage of entire unit including refrigeration compressors.

EXTRA MATERIALS

Provide one set of filters under provisions of Section 23 00 00.

PRODUCTS

General Requirements

Computer room air conditioners are to be packaged-type, freestanding units complete with internal wiring, piping, and controls.

Accessories Provided by Manufacturer:

Floor stand.

Water Detectors.

Smoke Detectors.

FLOOR-MOUNTED Units 6 tons AND LARGER

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Liebert Corporation

Compu-Aire

Data Aire

Description:  Packaged, factory assembled, prewired, and pre-piped; consisting of cabinet, fans, filters, humidifier, and controls.

Cabinet and Frame:  Welded steel, braced for rigidity, and supporting compressors and other mechanical equipment and fittings.

Doors and Access Panels:  Galvanized steel with polyurethane gaskets, hinges, and concealed fastening devices.

Insulation:  Thermally and acoustically insulated cabinet interior with 1-inch thick duct liner.

Finish of Exterior Surfaces: Baked-on, textured vinyl enamel; color as selected from manufacturer's standard colors.

Supply-Air Fan(s):

Fan shall be statically and dynamically balanced to minimize vibration in operation.

Motor shall be ODP or ECM per unit schedule.

Fan type shall be backward inclined housed centrifugal or plenum type per schedule.

Drive type: Direct or belt drive per unit schedule.

Belt Drive: V-belt, with steel shaft with self-aligning ball bearings and cast-iron or steel sheaves, variable- and adjustable-pitch motor sheave, minimum of two matched belts, with drive rated at a minimum of two times the nameplate rating of motor.

Refrigeration System:

Compressors: Variable speed hermetic scroll compressor with suction-gas-cooled motor with operating speed of 3500 rpm; thermal overloads; suction-line strainer; with oil strainer, internal motor overload protection, automatic-reset high-pressure switch, and pump-down low-pressure switch.

Refrigeration Circuits: Circuit will contain thermal-expansion valve with external equalizer, liquid-line solenoid valve, liquid-line filter-dryer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

Refrigerant:  R-407C or R-410A.

Refrigerant Evaporator Coil:  Refrigerant evaporator coil shall have capacity, number of rows, face velocity, and dimensions as scheduled. Coil shall be constructed with copper tubes and aluminum fins.

Mount coil assembly over stainless-steel drain pan and provide a condensate pump unit with integral float switch, pump-motor assembly, and condensate reservoir.

Remote Air-Cooled Refrigerant Condenser:  Corrosion-resistant cabinet, copper-tube aluminum-fin coils arranged for two circuits, multiple direct-drive propeller fans with permanently lubricated ball bearings, and single-phase motors with internal overload protection and integral electric control panel and disconnect switch.

Split system shall have suction- and liquid-line compatible fittings and refrigerant piping for field interconnection.

Electric-Resistance Heating Coil:  Finned-tube electric elements with contactor and high-temperature-limit switches.

Filter:  2-inch thick, disposable, glass-fiber media.

ASHRAE 52.2 MERV  7.

Integral Electrical Controls: Unit-mounted electrical enclosure with piano-hinged door, grounding lug, combination magnetic starters with overload relays, circuit breakers, cover interlock, and fusible control-circuit transformer.

Disconnect Switch:  Nonautomatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

Control System: Unit-mounted panel with main fan contactor, compressor contactor, compressor start capacitor, control transformer with circuit breaker, solid-state temperature- and humidity-control modules, humidity contactor, time-delay relay, heating contactor, and high-temperature thermostat.  Provide solid-state, wall-mounted control panel with start-stop switch, adjustable humidity set point, and adjustable temperature set point.

FLOOR-MOUNTED UNIts 5 tons AND SMALLER

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Liebert Corporation

Compu-Aire

Data Aire

Description:  Self-contained, factory assembled, prewired, and pre-piped; consisting of cabinet, fan, filters, and controls; for vertical floor mounting with ducted or plenum distribution.

Cabinet and Frame:  Welded tubular-steel frame with removable steel panels with baked-enamel finish, insulated with 1 inch thick duct liner.

Supply-Air Fan(s):

Fan shall be statically and dynamically balanced to minimize vibration in operation.

Motor shall be two speed permanent split

Fan type shall be backward inclined housed centrifugal or plenum type per schedule.

Drive type: Direct or belt drive per unit schedule.

Belt Drive: V-belt, with steel shaft with self-aligning ball bearings and cast-iron or steel sheaves, variable- and adjustable-pitch motor sheave, minimum of two matched belts, with drive rated at a minimum of two times the nameplate rating of motor.

Refrigeration System:

Compressors: Variable capacity hermetic scroll compressor; with suction-gas-cooled motor with operating speed of 3500 rpm; vibration isolators, thermal overloads; oil sight glass; suction-line strainer; and reversible oil pumps; with oil strainer, internal motor overload protection, resilient suspension system, crankcase heater, manual-reset high-pressure switch, and pump-down low-pressure switch.

Refrigeration Circuits: Circuit will contain thermal-expansion valve with external equalizer, liquid-line solenoid valve, liquid-line filter-dryer, sight glass with moisture indicator, service shutoff valves, charging valves, and charge of refrigerant.

Refrigerant:  R-407C or R-410A.

Refrigerant Evaporator Coil:  Refrigerant evaporator coil shall have capacity, number of rows, face velocity, and dimensions as scheduled. Coil shall be constructed with copper tubes and aluminum fins.

Mount coil assembly over stainless-steel drain pan and provide a condensate pump unit with integral float switch, pump-motor assembly, and condensate reservoir.

Remote Air-Cooled Refrigerant Condenser:  Integral, copper-tube aluminum-fin coil with centrifugal fan, belt driven.

Split system shall have suction- and liquid-line compatible fittings and refrigerant piping for field interconnection.

Electric-Resistance Heating Coil:  Finned-tube electric elements with contactor and high-temperature-limit switches.

Filter:  2-inch thick, disposable, glass-fiber media.

ASHRAE 52.2 MERV  7.

Disconnect Switch:  Nonautomatic, molded-case circuit breaker with handle accessible when panel is closed and capable of preventing access until switched to off position.

Control System: Unit-mounted panel with main fan contactor, compressor contactor, compressor start capacitor, control transformer with circuit breaker, solid-state temperature- and humidity-control modules, humidity contactor, time-delay relay, heating contactor, and high-temperature thermostat.  Provide solid-state, wall-mounted control panel with start-stop switch, adjustable humidity set point, and adjustable temperature set point.

FAN MOTORS

Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 23 05 13, Common Motor Requirements for HVAC Equipment.

Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Controllers, Electrical Devices, and Wiring:  Comply with requirements for electrical devices and connections specified in Division 26 Sections.

EXECUTION

INSTALLATION

Install computer-room air conditioners level and plumb, maintaining manufacturer's recommended clearances.

CONNECTIONS

Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

Install piping adjacent to machine to allow service and maintenance.

Water and Drainage Connections:  Comply with applicable requirements in Section 22 11 16, Domestic Water Piping Systems. Provide adequate connections for water-cooled units, condensate drain, and humidifier flushing system.

Refrigerant Piping:  Comply with applicable requirements in Section 23 23 00, Refrigerant Piping.  Provide shutoff valves and piping.

FIELD QUALITY CONTROL

Tests and Inspections:

Inspect for and remove shipping bolts, blocks, and tie-down straps.

After installing computer-room air conditioners and after electrical circuitry has been energized, test for compliance with requirements.

Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Computer-room air conditioners will be considered defective if they do not pass tests and inspections.

Prepare test and inspection reports.

After startup service and performance test, change filters and flush humidifier.

ADJUSTING

Adjust initial temperature and humidity set points.

Set field-adjustable switches and circuit-breaker trip ranges as indicated.

Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to two visits to Project during other-than-normal occupancy hours for this purpose.

END OF SECTION 23 81 23