|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 WWW.UTH.EDU |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 26 00 10

ELECTRICAL DEMOLITION

This Standard Specification Section is controlled by the Office of Facilities Planning and Construction, UT System.  It is to be used as guideline on all UT System projects, unless deviations are approved in writing by the Project Manager.  It is not to be used for bidding, permitting, construction or any other purpose.  This document is the property of UT System, and use of this document, in part or in whole, for any purpose other than for a UT System project may not be done without written permission of UT System.

To receive current updates of standard specification Sections, please go to the web site at: http://www.utsystem.edu/fpc or contact the Office of Facilities Planning and Construction by phone at (512) 499-4600 or by fax at (512) 499-4604.

The issuance and revision history of this Section is tabulated below.  Please destroy any previous copy in your possession

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | May 2002 | 4 | Original Release as OFPC Std. by James Da |
| 1 | Feb. 2003 | 4 | General revision per James Da |
| 2 | Jan. 2004 | 4 | General revision per James Da |
| 3 | Jan. 2006 | 4 | Revised Specification Numbers (CSI 2004) |
| 4 | June 2017 | 3 | Specification update |

The University of Texas at Arlington · The University of Texas at Austin · The University of Texas at Dallas · The University of Texas at El Paso

The University of Texas of the Permian Basin · The University of Texas Rio Grande Valley · The University of Texas at San Antonio

The University of Texas at Tyler · The University of Texas Southwestern Medical Center · The University of Texas Medical Branch at Galveston

The University of Texas Health Science Center at Houston · The University of Texas Health Science Center at San Antonio

The University of Texas MD Anderson Cancer Center · The University of Texas Health Science Center at Tyler

SECTION 26 00 10 – electrical demolition

GENERAL

WORK INCLUDED

Electrical demolition for remodeling.

Electrical portion of work covered by other Divisions for work pertaining to electrical demolition shall follow the requirements set forth by this specification.

RELATED WORK

This Section shall be used in conjunction with the following other specifications and related Contract Documents to establish the total requirements for minor electrical demolition for remodeling.

Section 26 00 00 - Basic Electrical Requirements.

In the event of conflict regarding minor electrical demolition requirements between this Section and any other Section, the provisions of this Section shall govern.

PRODUCTS

MATERIALS AND EQUIPMENT

Materials and equipment for patching and extending work:  as specified in individual Sections.

Provide all materials necessary for work.

EXECUTION

EXAMINATION

All demolitions or modifications to existing systems shall be coordinated through Owner’s Representative.  Demolition drawings are based on casual field observation and existing record documentations.  Therefore the accuracy or exactness of the drawings is not guaranteed.  The Contractor shall verify that field measurements and circuiting arrangements are as shown on Drawings and abandoned wiring and equipment serve only abandoned facilities.  The Contractor shall be responsible for reporting discrepancies to Engineer before disturbing existing installation.

Beginning of demolition means Contractor accepts existing conditions.

PREPARATION

Disconnect electrical systems in walls, floors, and ceilings scheduled for removal.  Provide temporary wiring and connections to maintain remaining systems in service during demolition and/or modification.    Owner reserves the right up to 24 hours prior to any scheduled event to delay or suspend shutdowns or outages to more convenient times at no additional cost.

Existing Electrical Service:  Maintain existing system in service until new system is complete and ready for service.  No work shall begin without proper permits and authorizations.  Disable system only to make switchovers and connections.  Obtain permission from Owner at least (2) weeks before partially or completely disabling system.  Minimize outage duration.  Make temporary connections to maintain service in areas adjacent to work area.

Existing Fire Alarm System:  Maintain existing system in service until new system is accepted.  Disable system only to make switchovers and connections.  Notify Owner at least (2) weeks before partially or completely disabling system.  Minimize outage duration.  Provisions for manual fire watch shall be provided in areas where services are interrupted.  Make temporary connections to maintain service in areas adjacent to work area.

Existing Telecommunications Systems:  Maintain existing systems in service until new systems are complete and ready for service.  Disable systems only to make switchovers and connections.  Notify Owner at least (2) weeks before partially or completely disabling systems.  Minimize outage duration.  Make temporary connections to maintain service in areas adjacent to work area.

DEMOLITION AND EXTENSION OF EXISTING ELECTRICAL WORK

Remove, relocate, and extend existing installations to accommodate new plan drawings.

Remove exposed abandoned conduit, including abandoned conduit above accessible ceiling finishes full length from source to device.  Cut embedded or concealed conduit flush with walls and floors, and patch surfaces.

Where source and devices span an area outside the scope of work, coordinate with Engineer of Record for scope of work associated with removing existing raceways. If existing raceways are permitted to remain, cap conduit at minimum 36” into an accessible location within the scope of work. Provide pull string for future use and label conduit ”SPARE-XXX-YYY” where “XXX” is the source equipment identifier and “YYY” is the room description and/or location of the source equipment.

Disconnect abandoned outlets and remove devices.  Remove abandoned outlets if conduit servicing them is abandoned and removed.  Provide blank cover for abandoned outlets that are not removed.

Disconnect and remove abandoned panelboards and distribution equipment.

Disconnect and remove electrical devices and equipment serving utilization equipment that has been removed.

Disconnect and remove abandoned luminaires.  Remove brackets, stems, hangers, and other accessories.

Repair adjacent construction and finishes damaged during demolition and extension work.

Maintain access to existing electrical installations that remain active.  Modify installation or provide access panel as appropriate.

Extend existing installations using materials and methods compatible with existing electrical installation or as specified.

The level of completion shall be demonstrated to Owner’s Representative.

Where equipment is indicated to be demolished and returned to Owner, the Contractor shall include the delivery of this equipment to the Owner's site storage area.  Remove with care all equipment to be relocated.  Repair or replacement of newly damaged equipment as a result of this project is the responsibility of the Contractor.

Clearly identify any existing shared neutrals that are scheduled to remain and that are associated with branch circuits included in the scope of work. Report the findings to Engineer of Record for review.

Where devices, luminaires, equipment and other associated electrical work are existing and scheduled to remain, the Contractor shall protect the systems for the duration of the project. Any damage sustained to the existing elements during the construction are the sole responsibility of the contractor.

CLEANING AND REPAIR

The Contractor shall follow Owner’s clean work policy and shall include the removal of trash and demolished material from the building or work area at the end of the each day and removal from the site once a week.

The Contractor shall be responsible for repairing adjacent construction and finishes damaged during demolition and/or modification.  The Contractor shall be responsible for the removal of ceiling tiles required in the demolition work.  The Contractor shall be responsible for the replacement of damaged tiles and reinstallation of the ceiling prior to final acceptance.

Panelboards:  Clean exposed surfaces and check tightness of electrical connections.  Replace damaged circuit breakers and provide closure plates for vacant positions.  Provide typed circuit directory showing revised circuiting arrangement.

Luminaires:  The following applies where indicated on the plans. Remove existing luminaires for cleaning.  Use mild detergent to clean all exterior and interior surfaces; rinse with clean water and wipe dry.  Replace lamps, ballasts, and broken electrical parts. Replacement ballasts shall utilize a quick disconnect to comply with NEC requirements for disconnect at luminaire.

DISPOSITION OF MATERIAL AND EQUIPMENT

Review with the Owner materials that have been removed and are no longer required, to determine any which the Owner may desire to keep.  Deliver those materials that the Owner desires to the Owner’s specified location.

For those materials not required by the Owner, dispose of them in accordance with applicable regulations.

END OF SECTION