|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 WWW.UTH.EDU |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 26 05 13

CABLE AND TERMINATIONS (MEDIUM VOLTAGE)

This Standard Specification Section is controlled by the Office of Facilities Planning and Construction, UT System.  It is to be used as guideline on all UT System projects, unless deviations are approved in writing by the Project Manager.  It is not to be used for bidding, permitting, construction or any other purpose.  This document is the property of UT System, and use of this document, in part or in whole, for any purpose other than for a UT System project may not be done without written permission of UT System.

To receive current updates of standard specification Sections, please go to the web site at: http://www.utsystem.edu/fpc or contact the Office of Facilities Planning and Construction by phone at (512) 499-4600 or by fax at (512) 499-4604.

The issuance and revision history of this Section is tabulated below.  Please destroy any previous copy in your possession

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 1 | June 2017 | 5 | New Specification Section |

The University of Texas at Arlington · The University of Texas at Austin · The University of Texas at Dallas · The University of Texas at El Paso

The University of Texas of the Permian Basin · The University of Texas Rio Grande Valley · The University of Texas at San Antonio

The University of Texas at Tyler · The University of Texas Southwestern Medical Center · The University of Texas Medical Branch at Galveston

The University of Texas Health Science Center at Houston · The University of Texas Health Science Center at San Antonio

The University of Texas MD Anderson Cancer Center · The University of Texas Health Science Center at Tyler

SECTION 26 05 13 - CABLE AND TERMINATIONS (MEDIUM VOLTAGE)

GENERAL

DESCRIPTION OF WORK

The extent of medium voltage cable work is indicated by drawings and by the requirements of this Section.

REFERENCES

AEIC CS6-96 – Specifications for Ethylene Propylene Rubber Insulated Shielded Power Cables Rated 69 kV.

ASTM B8-04 - Standard Specification for Concentric-Lay-Stranded Copper Conductors, Hard, Medium-Hard, or Soft.

ICEA S-93-639/NEMA WC74 – Shielded Power Cables Rated 5 – 46 kV.

ICEA S-97-682 – Utility Shield Power Cables Rated 5 - 46 kV.

IEEE 48 – Standard Test Procedures and Requirements for Alternating-Current Cable Terminations 2.5 kV through 765 kV.

UL 1072 – Medium-Voltage Power Cables.

IEEE 400 – Guide for Field Testing and Evaluation of the Insulation of Shielded Power Cable Systems.

AEIC No. 6 - Specifications for Ethylene-Propylene-Rubber-Insulated Power Cables 5,000 to 35,000 Volts.

ANSI/IEEE 386 - Separable Insulated Connectors for Power Distribution Systems Above 600 Volts.

ANSI/UL 83 - Thermoplastic-Insulated Wires and Cables.

ANSI/UL 1072 - Medium-Voltage Power Cables.

IEEE No. 48 - Standard Test Procedures and Requirements for High-Voltage Alternating-Current Cable Terminations.

ICEA S 61 402 (NEMA WC 5) - Thermoplastic-Insulated Wire and Cable for the Transmission and Distribution of Electrical Energy.

ICEA S 68 516 (NEMA WC 8) - Ethylene-Propylene-Rubber-Insulated Wire and Cable for the Transmission and Distribution of Electrical Energy.

QUALITY ASSURANCE

Manufacturer shall be a firm specializing in manufacturing medium voltage cable and accessories with minimum ten years documented experience.

Installer shall be a firm with at least five years of successful installation experience on projects with electrical work similar to that required for this project.

NEC Compliance: Comply with the National Electrical Code (NFPA 70) as applicable to construction and installation of electrical cable, and terminations required for this project.

Product Delivery, Storage Handling:

Provide factory wrapped waterproof flexible barrier materials for covering cable on wooden reels.  Cable ends shall be properly sealed to prevent water propagation.

Store cable in factory finished covering and in clean, dry place which provides protection against weather.

SUBMITTALS

Provide submittals in accordance with and in additional to Section 26 00 00 Basic Electrical Requirements, and Division 01 for submittal requirement.

Submit evidence documenting manufacturer’s ten-year experience in medium voltage cable and accessories manufacturing. Submit manufacturer's data on electrical cable and terminations.

Submit a list of previous work evidencing at least five years’ experience in medium voltage cable installation of similar type.

Submit name and experience record of each person to be engaged in medium voltage cable work.  Only those persons accepted by the Owner will be permitted to engage in medium voltage cable work.

Submit three copies of cable manufacturers' certified test report prior to installation of cable.

Submit original and two copies of certified field test report.

15 kV insulated conductor, splicing and terminating materials.

PRODUCTS

CABLE (MEDIUM VOLTAGE)

Provide cable and terminations of manufacturer's standard materials as indicated by published product information designed and constructed as recommended by the manufacturer and as required by the application.

Size.  As shown on the drawings.

Single Conductor Construction.

Single uncoated annealed copper conductor with Class B stranding.

Extruded semi-conducting thermosetting conductor screen firmly bonded to the overlaying insulation.

Ethylene-propylene-rubber (EPR) insulation 220 mils thick.

Extruded semi-conducting thermosetting insulation screen.

Copper shielding tape 5 mils thick helically applied with a minimum 12.5 percent overlap or 6 corrugated drain wires embedded in jacket.

Polyvinyl chloride jacket 80 mils thick.

Cable reel shall bear a tag containing name of manufacturer, UL label, cable type and year and month of manufacture.  Cable shall be imprinted with name of manufacturer, UL label, cable type and year and month of manufacture.

Cable to be furnished in continuous length and shall be free of kinks and defects at time of delivery to jobsite.

Provide stranded copper ground conductor in each conduit with phase conductors.  Size for ground conductor shall be as shown on the Drawings.

Medium voltage terminations shall be as follows:

Elbow Terminators:

200 amperes, load break, equal to Elastimold Type 165LR series with shield terminator with appropriate shield adapt kit.

600 amperes, non-load break, equal to Elastimold Type 655LR with shield terminator with appropriate shield adapt kit.

Indoor and outdoor terminators where required shall be equal to 3M Type QT-III with shield terminator.

Compatibility.  Terminating materials must be compatible with the cable supplied.  Submit proof of the acceptability by the cable manufacturer of any splicing or terminating materials.

Electrical tapes shall be equal to those manufactured by 3M as follows:

Fire Retardant Electric Arc Proofing:  Scotch 77.

Glass Cloth:  Scotch 69.

Self-fusing Silicone Rubber:  Scotch 70.

Vinyl Plastic:  Scotch 88.

High Voltage Factory Test.

Corona level test with a maximum partial discharge of 5 picocoulombs.

AC test:  33 kV for 5 minutes.

DC test:  80 kV for 15 minutes.

Insulation resistance test:  IR constant to be 50,000 megohms per 1000 feet minimum.

Use test procedures given in ICEA S-68-516 and AEIC No. 6.

Certified test reports with test data and corona level plots are to be submitted for review prior to shipment.

Engineer may witness test.

Type.  Single Conductor.  MV 105.

Listing.  UL 1072.

Acceptable Manufacturers.  Okonite, Southwire, Prysmian, Kerite.

EXECUTION

INSPECTION

Examine areas and conditions under which medium voltage cable terminations are to be installed and notify the Architect/Engineer in writing of conditions detrimental to the proper and timely completion of the work.  Do not proceed with the work until unsatisfactory conditions have been corrected.

INSTALLATION

Install medium voltage cable and terminations as indicated in accordance with the manufacturer's written instructions, the applicable requirements of NEC and the National Electrical Contractors Association's "Standard of Installation", and in accordance with recognized industry practices to ensure that products serve the intended functions.

Conduit shall be swabbed to ensure debris free.  Rubber duct swabs shall be sized to conduit used.  Do not exceed cable pulling tensions and bending radius recommended cable manufacturer.

Cable lubricant used on pulls shall be appropriate type or as specified by cable manufacturer.  All conduits shall be pre-lubricated with lubricant placed in each conduit ahead of a rubber duct swab and pulled in just before each cable pull.

Ground cable shield at each termination.

Medium Voltage Cable Identification:

Identify cables as to phase and circuit at each accessible location.  Identification to be accomplished by means of brass tags permanently affixed to cable embossed in letters no less than 1/2" high.

Arrange tags such that they can be read without moving cables.

Fireproof exposed medium voltage cable at transformers and switchgear as follows:

Apply one half-lapped wrap of fire retardant electric arc proofing tape over exposed areas of cable extended one inch into ducts.

Secure ends of fireproofing tape with two wraps of glass cloth tape.

Where cable terminates in a stress cone, wrap exposed insulation with half-lapped layer of self-fusing silicone tape applied without stretch.  Secure ends of silicone tape with vinyl plastic tape to prevent ravel.

Damaged cable jacket and/or insulation will be cause for rejection of cable.  Do not install cable if jacket is damaged in any way.  No kinks are permitted and the bends are to be kept in accordance with the minimums recommended by the manufacturer.  Pull cables directly into the duct from the coil or reel on which they are received.  Cable shall not be pulled off and laid on the ground prior to installation.  Make pulls in one direction.

Splices are not permitted for straight new pulls.  Contractor shall pull all cables in continuous lengths unless splices are specified by the Engineer.  Splices are permitted only where indicated on the Drawings for connections to existing underground medium voltage feeders.  The installer shall be a trained and certified technician for such special installation with appropriate splicing kit and materials.

Provide cable lengths with liberal allowances for slack for terminating.  If pulling grips are used, sufficient excess cable shall be allowed so that damage due to the pulling grips can be removed prior to terminating.  Use rubber tape to seal cable ends.  Cable shall not be pulled with the ends open.  Where cable requires more than one pull, the Contractor shall lay down new 6-mil PVC plastic sheathing on the ground in the lay down area.  The cable shall not be dragged across this surface, but will be permitted to be laid on the surface between pulls.  Cable ends shall be moisture proofed at all times until terminations are installed.

Provide pull-in guides, cable feeders or draw-in protectors to prevent damage to the cable at the duct mouths.  Pull cable by grips on the conductors with proper taping of the insulation to prevent pushback.  Short lengths may be pulled with cable grips around the entire group; however, care should be taken to ensure equal distribution of tension and any damaged ends must be cut off and discarded before terminating the cable.

Stop pulling instantly if undue tension occurs.  Lubricant shall be used to facilitate pulling and shall be compatible with the type of cable used.

Identify individual phases of each power circuit at points near each end of the cables.  Before connections are made at cable terminals, check by ringing out or talking over each conductor by means of a portable hand telephone set.  Identify circuits before terminal connections are made by one of the methods specified above.

PRIMARY CABLE TESTING

The cable manufacturer shall perform non-destructive factory tests on all cable in accordance with ICEA standards and shall furnish three copies of certified test report.

Cables shall be field tested prior to energization.  Notify the Architect/Engineer at the proper time during construction that the cables are ready for field testing.  Cables shall not be energized prior to testing.

Each circuit shall be rung-out or talked-out with proper signaling devices and with all equipment disconnected at each end to indicate that it is a continuous circuit where the operating requirements are that it shall be continuous.

Insulation resistance of each cable shall be measured with a 500 volt megohm meter.  Cable will be rejected if resistance is less than 25 megohms.

All power cables shall be given d-c high potential tests after terminations have been made, but before connections have been made to busses or apparatus according to IEEE 400 and manufacturer's recommendation.

Apply test voltage to conductors in at least five equal increments to maximum test voltage.  Duration at each step should be long enough for the current to reach steady value.

Record leakage current at each increment, allowing for charging current decay.  Hold maximum test voltage for 15 minutes.  Current magnitudes should be recorded at 2 minutes and 15 minutes after the maximum test voltage has been reached.

Record results of test in tabular form and in plots of current versus time for incremental voltages, and current versus time at maximum voltage.

Adequate means shall be taken to insure safety during the tests and all safety instructions of the test operator shall be carried out.

If a cable fails, the fault shall be located, and all cables in that conduit between the nearest pulling points on each side of the failure shall be withdrawn.  If, in the opinion of the Owner, the other cables in the same conduit have not been damaged, they may be reinstated, but the cable which failed shall be replaced by new cable.  After the replacement of the faulted cable, and any other damaged cables, all cables of the circuit in that conduit shall be retested.

During the period of warranty any failure in primary cable, terminations or splices shall require immediate correction.  In the event of a failure creating interruption in electrical service, furnish and install all labor and materials for temporary services to get the electrical system back in service.  Work shall begin immediately upon notification of a failure, regardless of time.

END OF SECTION