|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 WWW.UTH.EDU |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 26 05 73

PROTECTIVE RELAY AND DEVICE COORDINATION

This Standard Specification Section is controlled by the Office of Facilities Planning and Construction, UT System.  It is to be used as guideline on all UT System projects, unless deviations are approved in writing by the Project Manager.  It is not to be used for bidding, permitting, construction or any other purpose.  This document is the property of UT System, and use of this document, in part or in whole, for any purpose other than for a UT System project may not be done without written permission of UT System.

To receive current updates of standard specification Sections, please go to the web site at: http://www.utsystem.edu/fpc or contact the Office of Facilities Planning and Construction by phone at (512) 499-4600 or by fax at (512) 499-4604.

The issuance and revision history of this Section is tabulated below.  Please destroy any previous copy in your possession

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 1 | June 2017 | 7 | New Specification Section |

The University of Texas at Arlington · The University of Texas at Austin · The University of Texas at Dallas · The University of Texas at El Paso

The University of Texas of the Permian Basin · The University of Texas Rio Grande Valley · The University of Texas at San Antonio

The University of Texas at Tyler · The University of Texas Southwestern Medical Center · The University of Texas Medical Branch at Galveston

The University of Texas Health Science Center at Houston · The University of Texas Health Science Center at San Antonio

The University of Texas MD Anderson Cancer Center · The University of Texas Health Science Center at Tyler

SECTION 26 05 73 - OVERCURRENT PROTECTIVE DEVICE AND ARC FLASH STUDY

GENERAL

SUMMARY

Provide a complete short-circuit and protective device coordination study for the normal and emergency/standby power electrical distribution systems.

- [NOTE TO SPEC WRITER: coordinate with Engineer of Record and Owner’s Representative for extent and include description here]

The contractor shall furnish an Arc Flash Hazard Analysis Study per the requirements set forth in the latest edition of NFPA 70E - Standard for Electrical Safety in the Workplace. The arc flash hazard analysis shall be performed according to the IEEE 1584 equations that are presented in the latest edition of NFPA70E, Annex D. The arc flash study shall encompass all normal and emergency/standby power electrical distribution systems with the exception, of any equipment as described in paragraph 2.04C.

SUBMITTALS

A preliminary short-circuit study shall be submitted to the design engineer either before or at the same time as the equipment submittals. If equipment submittals such as switchgear, switchboards, panelboards etc. are submitted without a preliminary study, they will be returned as rejected. .

The results of the short-circuit, protective device coordination and arc flash hazard analysis studies shall be summarized in a final report. The report shall include the following sections:

Executive Summary.

Descriptions, purpose, basis and scope of the study.

Tabulations of circuit breaker, fuse and other protective device ratings versus calculated short circuit duties.

Protective device time versus current coordination curves, tabulations of relay and circuit breaker trip unit settings, fuse selection.

Fault current calculations including a definition of terms and guide for interpretation of the computer printout.

Details of the incident energy and flash protection boundary calculations.

Recommendations for system improvements, where needed.

One-line diagram.

Arc flash labels shall be provided for all equipment described in paragraph 2.04.

REFERENCES

Institute of Electrical and Electronics Engineers, Inc. (IEEE):

IEEE 141 – Recommended Practice for Electric Power Distribution and Coordination of Industrial and Commercial Power Systems.

IEEE 242 – Recommended Practice for Protection and Coordination of Industrial and Commercial Power Systems.

IEEE 399 – Recommended Practice for Industrial and Commercial Power System Analysis.

IEEE 241 – Recommended Practice for Electric Power Systems in Commercial Buildings.

IEEE 1015 – Recommended Practice for Applying Low-Voltage Circuit Breakers Used in Industrial and Commercial Power Systems.

IEEE 1584 - Guide for Performing Arc-Flash Hazard Calculations.

American National Standards Institute (ANSI):

ANSI C57.12.00 – Standard General Requirements for Liquid-Immersed Distribution, Power, and Regulating Transformers.

ANSI C37.13 – Standard for Low Voltage AC Power Circuit Breakers Used in Enclosures.

ANSI C37.010 – Standard Application Guide for AC High Voltage Circuit Breakers Rated on a Symmetrical Current Basis.

ANSI C 37.41 – Standard Design Tests for High Voltage Fuses, Distribution Enclosed Single-Pole Air Switches, Fuse Disconnecting Switches and Accessories.

The National Fire Protection Association (NFPA)

NFPA 70 - National Electrical Code.

NFPA 70E – Standard for Electrical Safety in the Workplace.

QUALIFICATIONS

The short-circuit, protective device coordination and arc flash hazard analysis studies shall be conducted under the supervision and approval of a Licensed Professional Electrical Engineer licensed in the state of Texas and skilled in performing and interpreting the power system studies.

The Licensed Electrical Engineer shall be a full-time employee of the equipment manufacturer or an approved engineering firm and have a minimum of five (5) years of experience in performing power system studies.

COMPUTER ANALYSIS SOFTWARE

The studies shall be performed using the latest revision of EDSA, SKM Systems Analysis Power Tools or ETAP, unless approved otherwise.

PRODUCTS

DATA COLLECTION

The Contractor shall be responsible for collecting all data for the studies as directed by the Engineer of Record.

SHORT-CIRCUIT AND PROTECTIVE DEVICE EVALUATION STUDY

Provide the following:

Calculation methods and assumptions.

Selected base per unit quantities.

One-line diagram of the system being evaluated.

Source impedance data, including electric utility system and motor fault contribution characteristics.

Tabulations of calculated quantities.

Results, conclusions, and recommendations.

Calculate short-circuit momentary and interrupting duties for a three-phase bolted fault and a line to ground fault at each piece of equipment/bus as described in 1.01.

Protective Device Evaluation:

Evaluate equipment and protective devices and compare to short circuit ratings.

Adequacy of all equipment to withstand short-circuit stresses.

Use actual conductor impedances if known. If unknown, use typical conductor impedances based on IEEE Standard 141-1993.

Transformer design impedances shall be used only when test impedances are not available.

PROTECTIVE DEVICE COORDINATION STUDY

Proposed protective device coordination time-current curves (TCC) shall be displayed on log-log scale graphs. The phase curves shall be plotted on separate sheets from the ground fault curves.

Plot the following characteristics on the TCC graphs where applicable:

Equipment name based on Bid documents.

Electric utility’s overcurrent protective device.

Medium voltage (4.16kV and above) equipment overcurrent relay settings.

Medium and low voltage fuses including manufacturer’s minimum melt, total clearing, tolerance, and damage bands.

Low voltage (480V and below) equipment circuit breaker trip device settings, including manufacturer’s tolerance bands.

Transformer full-load current, magnetizing inrush current and ANSI through-fault protection curves.

Ground fault protective devices, as applicable.

Pertinent motor starting characteristics and motor damage points, where applicable.

Pertinent generator short-circuit decrement curve and generator damage point.

Provide adequate time margins between device characteristics such that selective operation is provided, while providing proper protection.

[ESSENTIAL][EMERGENCY] ELECTRICAL SYSTEM:

The [essential][emergency] distribution system shall be selectively coordinated down to [ NOTE TO SPEC WRITER: Engineer of Record and Owner’s Representative to agree on time if less than 0.1 ]0.1 seconds. System will be coordinated from main service entrance through the largest branch circuit device.  Selective coordination must be provided for the system throughout the entirety of both the normal and emergency branches.

ARC FLASH HAZARD ANALYSIS

The arc flash hazard analysis shall be performed according to the IEEE 1584-2002 equations that are presented in NFPA 70E, Annex D.

The flash protection boundary and the incident energy shall be calculated at all significant locations in the electrical distribution system (switchboards, switchgear, motor-control centers, panelboards, busway and splitters) where work could be performed on energized parts.

The Arc-Flash Hazard Analysis shall include all electrical equipment. [NOTE TO SPEC WRITER:  after coordination with Engineer of Record and Owner’s Representative, include any exceptions here.]

Minimum working distances shall be based upon the calculated arc flash boundary considering incident energy of 1.2 cal/cm2.

The results of the short circuit calculations (fault values) and protective device coordination study (device clearing times) shall be utilized for use by the arc flash program.  Ground overcurrent relays should not be taken into consideration when determining the clearing time when performing incident energy calculations

The short-circuit calculations and the corresponding incident energy calculations for multiple system scenarios must be compared and the greatest incident energy must be uniquely reported for each equipment location. Calculations must be performed to represent the maximum and minimum contributions of fault current magnitude for all normal and emergency operating conditions. The minimum calculation will assume that the utility contribution is at a minimum and will assume a minimum motor contribution (all motors off).  Conversely, the maximum calculation will assume a maximum contribution from the utility and will assume the maximum amount of motors to be operating.

The incident energy calculations must consider the accumulation of energy over time when performing arc flash calculations on buses with multiple sources. Iterative calculations must take into account the changing current contributions, as the sources are interrupted or decremented with time. Fault contribution from motors and generators should be decremented as follows:

Fault contribution from induction motors should not be considered beyond 5 cycles.

Fault contribution from synchronous motors and generators should be decayed to match the actual decrement of each as closely as possible.

For all equipment locations with a separately enclosed main device (where there is adequate separation between the line side terminals of the main protective device and the work location), calculations for incident energy and flash protection boundary shall include both the line and load side of the main breaker.

When performing incident energy calculations on the line side of a main breaker (as required per above), the line side and load side contributions must be included in the fault calculation.

Mis-coordination should be checked amongst all devices within the branch containing the immediate protective device upstream of the calculation location and the calculation should utilize the fastest device to compute the incident energy for the corresponding location.

Arc Flash calculations shall be based on the actual overcurrent protective device clearing time. Maximum clearing time will be capped at 2 seconds based on IEEE 1584-2002 section B.1.2. Where it is not physically possible to move outside of the flash protection boundary in less than 2 seconds during an arc flash event, a maximum clearing time based on the specific location shall be utilized.

REPORT SECTIONS

Input data shall include, but not be limited to the following:

Feeder input data including feeder type (cable or bus), size and length, number per phase, conduit type (magnetic or non-magnetic) and conductor material (copper or aluminum).

Transformer input data, including winding connections, secondary neutral-ground connection, primary and secondary voltage ratings, kVA rating, impedance, % taps and phase shift.

Reactor data, including voltage rating, and impedance.

Generation contribution data, (synchronous generators and Utility), including short-circuit sub-transient reactance (X”d), rated MVA, rated voltage, three-phase and single line-ground contribution (for Utility sources) and X/R ratio.

Motor contribution data (induction motors and synchronous motors), including short-circuit reactance, rated horsepower or kVA, rated voltage, and X/R ratio.

Short-Circuit Output Data shall include, but not be limited to the following reports:

Low Voltage Fault Report shall include a section for three-phase and unbalanced fault calculations and shall show the following information for each applicable location:

Voltage.

Calculated fault current magnitude and angle.

Fault point X/R ratio.

Equivalent impedance.

Momentary Duty Report shall include a section for three-phase and unbalanced fault calculations and shall show the following information for each applicable location:

Voltage.

Calculated symmetrical fault current magnitude and angle.

Fault point X/R ratio.

Calculated asymmetrical fault currents:

Based on fault point X/R ratio.

Based on calculated symmetrical value multiplied by 1.6.

Based on calculated symmetrical value multiplied by 2.7.

Equivalent impedance.

Interrupting Duty Report shall include a section for three-phase and unbalanced fault calculations and shall show the following information for each applicable location:

Voltage.

Calculated symmetrical fault current magnitude and angle.

Fault point X/R ratio.

No AC Decrement (NACD) Ratio.

Equivalent impedance.

Multiplying factors for 2, 3, 5 and 8 cycle circuit breakers rated on a symmetrical basis.

Multiplying factors for 2, 3, 5 and 8 cycle circuit breakers rated on a total basis.

Recommended Protective Device Settings:

Phase and Ground Relays:

Current transformer ratio.

Current setting.

Time setting.

Instantaneous setting.

Recommendations on improved relaying systems, if applicable.

Circuit Breakers:

Adjustable pickups and time delays (long time, short time, ground).

Adjustable time-current characteristic.

Adjustable instantaneous pickup.

Recommendations on improved trip systems, if applicable.

Incident Energy and Flash Protection Boundary Calculations:

Arcing fault magnitude.

Protective device clearing time.

Duration of arc.

Arc flash boundary.

Working distance.

Incident energy.

Hazard Risk Category.

Recommendations for arc flash energy reduction.

EXECUTION

FIELD ADJUSTMENT

Submit report to engineer for review. Based upon the Engineer and Utility Provider’s review, incorporate comments and required adjustments into final round of adjustments at all devices.

Adjust relay and protective device settings according to the recommended settings table provided by the coordination study. Field adjustments to be completed by, or under the direction of the engineering service division of the equipment manufacturer.

Making minor modifications to equipment as required to accomplish conformance with short circuit and protective device coordination studies to be coordinated with Engineer of Record and equipment manufacturer.

ARC FLASH WARNING LABELS

The contractor of the Arc Flash Hazard Analysis shall provide a 3.5 in. x 5 in. thermal transfer type label of high adhesion polyester for each work location analyzed.

All labels will be based on recommended overcurrent device settings and will be provided after the results of the analysis have been presented to the owner and after any system changes, upgrades or modifications have been incorporated in the system.

The label shall include the following information, at a minimum:

Location designation.

Nominal voltage.

Flash protection boundary.

Hazard risk category.

Incident energy.

Working distance.

Engineering report number, revision number and issue date.

Labels shall be machine printed, with no field markings.

Arc flash labels shall be provided in the following manner and all labels shall be based on recommended overcurrent device settings. See page 6 for example of arc flash label.

For each 480V and 208V panelboard, one arc flash label shall be provided.

For each motor control center, one arc flash label shall be provided for each section.

For each low voltage switchboard, one arc flash label shall be provided for each section.

For each low and medium voltage switchgear, one flash label shall be provided for each breaker.

For medium voltage switches one arc flash label shall be provided

Labels shall be field installed by the engineering service division of the equipment manufacturer under the Startup and Acceptance Testing contract portion.

ARC FLASH TRAINING

- NOTE TO SPEC WRITER:  COORDINATE WITH OWNER FOR THE NEED, DESIRE OR THE EXTENT OF TRAINING:

- The contractor of the Arc Flash Hazard Analysis shall train the owner’s qualified electrical personnel of the potential arc flash hazards associated with working on energized equipment (minimum of 4 hours). The training shall be certified for continuing education units (CEUs) by the International Association for Continuing Education Training (IACET) or equivalent.

END OF SECTION