|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 WWW.UTH.EDU |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 26 12 13

SECONDARY SUBSTATION TRANSFORMERS

This Standard Specification Section is controlled by the Office of Facilities Planning and Construction, UT System.  It is to be used as guideline on all UT System projects, unless deviations are approved in writing by the Project Manager.  It is not to be used for bidding, permitting, construction or any other purpose.  This document is the property of UT System, and use of this document, in part or in whole, for any purpose other than for a UT System project may not be done without written permission of UT System.

To receive current updates of standard specification Sections, please go to the web site at: http://www.utsystem.edu/fpc or contact the Office of Facilities Planning and Construction by phone at (512) 499-4600 or by fax at (512) 499-4604.

The issuance and revision history of this Section is tabulated below.  Please destroy any previous copy in your possession

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | Jan. 1996 | 5 | Last Revision |
| 1 | Sept. 2004 | 7 | General revision |
| 2 | May 2005 | 7 | General revision per James Da |
| 3 | Jan. 2006 | 7 | Revised Specification Numbers (CSI 2004) |
| 4 | June 2017 | 6 | Specification update |

The University of Texas at Arlington · The University of Texas at Austin · The University of Texas at Dallas · The University of Texas at El Paso

The University of Texas of the Permian Basin · The University of Texas Rio Grande Valley · The University of Texas at San Antonio

The University of Texas at Tyler · The University of Texas Southwestern Medical Center · The University of Texas Medical Branch at Galveston

The University of Texas Health Science Center at Houston · The University of Texas Health Science Center at San Antonio

The University of Texas MD Anderson Cancer Center · The University of Texas Health Science Center at Tyler

SECTION 26 12 13 – SECONDARY SUBSTATION TRANSFORMERS – LIQUID FILLED

GENERAL

WORK INCLUDED

Indoor or outdoor liquid filled secondary substation transformers (medium voltage) for rating and installation as indicated on Drawings.

The indoor substation type liquid-filled transformers are part of a unit substation that also consists of low-voltage metal-enclosed switchgear.  All equipment in the unit substation shall be products of the same manufacturer who furnishes the low voltage metal-enclosed switchgear.  The liquid fill of indoor transformers shall be less-flammable.

RELATED WORK

Section 26 24 13 - Switchboards

Section 26 13 00 - Metal-Enclosed Switchgear (Medium Voltage)

Section 26 05 26 - Grounding

REFERENCES

IEEE C57.12.00 - General Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers

ANSI C57.12.10 – Requirements for Transformers 230 kV and Below

IEEE C57.12.70 – Terminal Markings and Connections for Distribution and Power Transformers

IEEE C57.12.90 - Test Code for Liquid-Immersed Distribution, Power, and Regulating Transformers

IEEE C57.98 – Guide for Transformer Impulse Tests

IEEE C57.109 – Guide for Liquid Immersed Transformer Though-Fault-Current Duration

IEEE C57.111 – Guide for Acceptance of Silicon Insulating Fluid and Its Maintenance in Transformers

IEEE C57.121 – Guide for Acceptance and Maintenance of Less Flammable Hydrocarbon Fluid in Transformers

NEMA TR1:	Transformers, Regulators, and Reactors

SUBMITTALS

Provide submittals in accordance with and in additional to Section 26 00 00, Basic Electrical Requirements, and Division 01 for submittal requirement.

Manufacturer and year manufactured

Outline dimensions including plan and elevation views, base plan, and conduit entry (top or bottom) opening dimensions.

Support points, locations of all accessories, bushings, and terminal compartments.

Transformer diagrammatic nameplate (each unit) including manufacturer, primary voltage and connections, secondary voltage and connections, rated KVA, number of phases, number and percent taps, frequency and percent impedance.

Schematic and interconnection diagrams for control and monitoring devices.

Location for floor channels, anchor bolts, drain valve, and ground pads.

Total weight of unit (transformer and filling liquid).

Transformer winding temperature rise.

Filling liquid capacity in gallons.

Bill of material showing components, ratings, and part numbers.

Product descriptive literature including standard factory tests for each unit, and options for similar units.

Short-circuit withstand capacities.

Material safety data sheet for insulating liquid.

Submit dimensioned drawings of transformers, including support points, lifting eyes and brackets.

Submit the following information as a complete set in 3-ring binder after fabrication, assembly, delivery, installation, and field testing.  Deliver to Owner no later than the training included in the contract.

Operation and Maintenance manual.

Maintenance schedule for the first cycle of scheduled maintenance, not less than 12 months.

Spare parts list, renewable parts list, and consumable list.

As-built drawings including final fabrication drawings of items specified in 1.4, this Section.

Certified test reports.

DELIVERY, STORAGE AND HANDLING

Store in a clean dry location.

Handle transformers using only lifting eyes and brackets provided for handling purposes.  Protect units against damage from rain, sleet, or snow if handled in inclement weather.

PRODUCTS

SECONDARY SUBSTATION TRANSFORMERS

Transformers shall be equipped with a [close-coupling] [air filled terminal compartment] on the high voltage side, and a [close-coupling] [air filled terminal compartment] on the low voltage side.

[***NOTE TO SPEC WRITER: COMPLETE TRANSFORMER RATINGS IN PARAGRAPH "B" BELOW].

The ratings of each transformer shall be as follows:

#### KVA Rating: [______ ] [______/______] [OA] [OA/FA], 3PH, 60HZ

#### Temp. Rise:  The average temperature rise of the windings measured by the resistance method, shall be [65°] [55°] C when the transformer is operated at rated KVA output in a 40º C ambient, without loss of life expectancy.

#### Impedance:  5.75%+ or per drawings.

#### H. Voltage: ______ [delta] [wye]

#### H.V. BIL:   ______ KV

#### H.V. Taps:  2 - 2-1/2% full capacity above and below rated voltage

#### L. Voltage: ______ [delta] [wye]

#### L.V. BIL:   ______ KV

[***NOTE TO SPEC WRITER:  SELECT APPROPRIATE LIQUID IN PARAGRAPH "C" BELOW USE ONLY NON-FLAMMABLE LIQUID FOR INDOOR APPLICATIONS].

The units shall be [silicone] [mineral oil] [high fire point hydrocarbon R-Temp fluid] filled and shall be in accordance with the National Electrical Code.  The insulating liquid shall be shipped in the tank of the transformer.

[***NOTE TO SPEC WRITER:  SELECT PARAGRAPH "D" BELOW IF APPROPRIATE TO THE DESIGN.}

Transformers shall include all devices, wiring, fans and auxiliary equipment necessary for automatic temperature controlled forced-air cooling.  Control power for fans shall be 230 volt AC, single phase, furnished from a control transformer in the secondary switchgear.

The transformers shall be designed to carry short time emergency overloads in accordance with ANSI standards.  Duration and magnitude of designed short circuit withstand capability shall be as outlined in IEEE C57.12.00.

Transformer features and accessories shall include:

De-energized tap changer with cover mounted, externally operated, pad lockable handle;

Liquid temperature indicator with maximum indicating hand and alarm contacts;

Combination drain and filter valve and sampling device;

Manual gas pressure test connection;

1" filling plug and filter press connection in cover;

Top liquid thermometer (dial type), with alarm contacts, connected to Building Automation System (BAS);

Magnetic liquid level gauge, with low level alarm contacts, connected to BAS;

Provision for lifting;

Provision for jacking on tank or base;

Base for skidding or rolling in two directions;

Automatic pressure relief device that automatically reseals after operation, with alarm contacts, connected to BAS;

Sudden pressure relay with tripping/alarm contacts, connected to BAS;

Ground pad;

Instruction and diagrammatic nameplate;

Pressure vacuum gauge;

Welded-on main tank cover and handhole in cover;

Bushings per ANSI Standards with copper conductors and terminals.  Bushing may be [cover mounted] or [left/right] oriented.

Flexible bus braid connections, terminals, and fasteners for connecting the transformer secondary and the substation, rated for the maximum transformer ampacity configuration.

Primary selective switching scheme as indicated in drawings.

Windings shall be wound with [copper] [aluminum] conductors.

The main transformer tank and attached components shall be designed to withstand pressures 25% greater than the design value without permanent deformation.  Construction shall be from carbon steel plate reinforced with external sidewall braces.  All seams and joints shall be continuously welded.

Each radiator assembly shall be individually welded and receive a quality control pressurized check for leaks.  The entire tank assembly shall receive a similar leak test before tanking.  A final six-hour leak test shall be performed after the transformer is tanked, welded and completed to ensure that there are no leaks before shipment.

[***NOTE TO SPEC WRITER:  EDIT PARAGRAPH "J" BELOW.]

[Indoor units shall be painted ANSI NO. 61 (light gray) [and] [outdoor units shall be painted ANSI NO. 24 (dark grey)].

Manufacturer shall perform the following tests on all transformers:

Resistance measurements of all windings on the rated voltage connection and at the tap extremes.

Ratio tests on the rated voltage connection and on all tap connections.

Polarity and phase-relation tests on the rated voltage connections.

No-load loss at rated voltage on the rated voltage connection.

Exciting current at rated voltage on the rated voltage connection.

Impedance and load loss at rated current on the rated voltage connection and on the tap extremes.

Applied potential tests.

Induced potential tests.

Temperature Test:

Furnish temperature tests for each size and type transformer.  Certified tests of a similar unit of identical size and type will be acceptable.

When a transformer is furnished with auxiliary cooling equipment to provide more than one KVA rating, temperature tests shall be made on both the lowest KVA OA rating and on the highest KVA FA rating.

All tests shall be conducted in accordance with the latest revision of ANSI C57.12.90 and NEMA TR2.

Furnish manufacturer's certified test report.

Owner reserves right to witness tests.  Provide four-week notice of testing schedule.

Audible sound level shall comply with NEMA TR1.

HIGH VOLTAGE COMPARTMENT

General.  Fabricate this compartment so as to enclose the high voltage bushings and provide for [bottom] [top] entrance of MV conductors.

Access.  Use a fastening device in the low voltage compartment that must be released to permit opening or removal of door to the high voltage compartment.

Surge Arresters. Provide distribution type surge arresters at transformers as shown on the plans. Furnish Metal-Oxide Varistor Elbow (MOVE) type arresters rated at [15 kV, 12.7kV MCOV] [6kV, 5.1kV MCOV][12kV, 10.2kV MCOV] .

Fuses. Provide oil immersed, load break, bayonet fuse holder with expulsion style fuses. In addition, provide an oil submersible protector with current limiting fuses rated for 50,000 AIC. Current limiting fuses shall be placed in series with expulsion fuses.

High Voltage Bushings. Provide 200A bushing wells, load-break bushing inserts and load break type separable [15 kV] [5kV] elbow connectors.

LOW VOLTAGE COMPARTMENT

General.  Fabricate this compartment so as to enclose the low voltage terminals and provide for [bottom] [top] entrance of conductors. Provide ample space for termination of incoming cables.

Access.  Make unit so that removing the padlock on the door, permits access to the low voltage compartment when the compartment door is opened.

Low Voltage Bushings.  Provide properly ANSI-rated bushings suitable for live-front stress cone termination of [5 kV] [600v] conductors.

EXECUTION

EXAMINATION

Verify that pads are ready to receive work.

Verify field measurements are as shown on Drawings and as indicated by manufacturer’s shop drawings.

Verify that required utilities are available, in proper location, and ready for use.

Beginning of installation means installer accepts conditions.

INSTALLATION

Install in accordance with manufacturer’s instructions.

Install safety labels to NEMA requirements.

Secondary containment for spill control maybe required.  Coordinate and comply such requirement with the Owner.

FIELD QUALITY CONTROL

Check for damage and tight connections prior to energizing transformers.  Check primary, secondary, and ground connections.

Clean and inspect bushings.

Inspect bushing clamps and gaskets.

Inspect cover and handhole gasket seals.

Inspect tap change seals.

Check fluid leaks and external damage to radiators.

Check liquid level.

Check accessory devices for condition and proper operation.

Measure primary and secondary voltages and make appropriate tap adjustments within zero to two percent of rated voltage at no load.

Check phase rotation and make appropriate changes in connection to match phase rotation between units connected in secondary-selective schemes.

Insulation resistance test:  Megger transformer windings high to low and ground, low to high and ground, and high and low to ground.

Perform turns ratio test.

Where auxiliary cooling has been provided, verify proper operation of such equipment.

Field test reports shall be forwarded to the Owner.

END OF SECTION