|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 WWW.UTH.EDU |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 26 22 13

DRY TYPE TRANSFORMERS

This Standard Specification Section is controlled by the Office of Facilities Planning and Construction, UT System.  It is to be used as guideline on all UT System projects, unless deviations are approved in writing by the Project Manager.  It is not to be used for bidding, permitting, construction or any other purpose.  This document is the property of UT System, and use of this document, in part or in whole, for any purpose other than for a UT System project may not be done without written permission of UT System.

To receive current updates of standard specification Sections, please go to the web site at: http://www.utsystem.edu/fpc or contact the Office of Facilities Planning and Construction by phone at (512) 499-4600 or by fax at (512) 499-4604.

The issuance and revision history of this Section is tabulated below.  Please destroy any previous copy in your possession

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 1 | Jan. 1996 | 5 | Last Revision |
| 2 | Nov. 2004 | 7 | General Revision |
| 3 | May 2005 | 7 | General revision per James Da |
| 4 | June 2017 | 5 | Specification update |

The University of Texas at Arlington · The University of Texas at Austin · The University of Texas at Dallas · The University of Texas at El Paso

The University of Texas of the Permian Basin · The University of Texas Rio Grande Valley · The University of Texas at San Antonio

The University of Texas at Tyler · The University of Texas Southwestern Medical Center · The University of Texas Medical Branch at Galveston

The University of Texas Health Science Center at Houston · The University of Texas Health Science Center at San Antonio

The University of Texas MD Anderson Cancer Center · The University of Texas Health Science Center at Tyler

SECTION 26 22 13 - DRY TYPE TRANSFORMERS

GENERAL

WORK INCLUDED

This Section includes enclosed dry type distribution transformers rated 600 volts and less, sizes up to 500 kVA.

Dry type Two-Winding transformers.

Dry type Buck and Boost transformers.

Dry type Shielded Isolation transformers.

Dry type, K-rated transformers.

REFERENCES

NEMA ST 1 - Specialty Transformers (Except General Purpose Type)

NEMA ST 20 - Dry Type Transformers for General Applications

IEEE C57.12.01 - General Requirements for Dry-Type Distribution and Power Transformers.

IEEE C57.12.91 - Test Code for Dry-Type Distribution and Power Transformers

IEEE C57.96 – Guide for Loading Dry-Type Distribution and Power Transformers

IEEE Std. 519 - Recommended Practices and Requirements for Harmonic Control in Electrical Power Systems

UL 506 – Specialty Transformers

UL 1561 - Dry Type General Purpose and Power Transformers

NEMA TP 1 – Guide for Determining Energy Efficiency for Distribution Transformers

NEMA TP 2 – Standard Test Method for Measuring the Energy Consumption for Distribution Transformers

SUBMITTALS

Provide submittals in accordance with and in additional to Section 26 00 00, Basic Electrical Requirements, and Division 01 for submittal requirement.

Submit manufacturer's data on dry type transformers, vibration isolators and accessories.

Include outline and support point dimensions of enclosures and accessories; unit weight; voltage; kVA; impedance ratings and characteristics; loss data; efficiency at 25, 50, 75 and 100 percent rated load; sound level; tap configurations; insulation system type, K-rating, and rated temperature rise.

PRODUCT DELIVERY, STORAGE AND HANDLING

Store transformers in a clean and dry space and protected from weather in accordance with manufacturer’s instructions.  Cover ventilating openings to keep out dust.

Transformer shall not be used as work tables, scaffolds or ladders.

Handle transformers carefully to avoid damage to material components, enclosure and finish.  Use only lifting eyes and brackets provided for that purpose.  Damaged transformers shall be rejected and not be installed on project.

PRODUCTS

MATERIALS AND EQUIPMENT

Transformers shall be of dry type complying with the design function requirements of the project.  Design characteristics shall be as noted in manufacturer's submittal data.

Provide barrel type coils vacuum impregnated with high grade insulating varnish, non-hydroscopic thermo-setting type.

Furnish [aluminum] [copper] windings, continuous without splice.

Use non-aging silicon steel cores held together with steel channels or angles, with low flux density, quiet operating, and vibration isolated from enclosure and support channels.

All transformers shall be designed, manufactured, and tested in accordance with all the latest applicable ANSI, NEMA, IEEE and UL standards, and shall be UL listed and bear the UL label.

DRY TYPE TWO-WINDING TRANSFORMERS

Acceptable manufacturers

Square D

Cutler-Hammer/Eaton

General Electric Company

Other manufacturers equal in design and function will be considered upon A/E approval following substitution procedure in 26 00 00, and Division 01 for substitution requirement.

Dry type transformers shall be NEMA ST 20; factory-assembled, air cooled dry type transformers; ratings as shown on the Drawings.

Insulation system and average winding temperature rise (in a 40 degree C maximum ambient) for rated kVA as follows:

| kVA Rating | Insulation Class (degree C) | Temperature Rise (degree C) |
| --- | --- | --- |
| 1-15 kVA | 185 | 115 |
| 25-500 kVA | 220 | 115 |

The maximum temperature of the top of the enclosure shall not exceed 50 degrees C rise above a 40 degree ambient.

Winding Taps, Transformers 15 kVA and Less:  Two 5 percent below rated voltage, full capacity taps on primary winding.

Winding Taps, Transformers 25 kVA and Larger:  Two 2.5 percent above rated voltage and four 2.5 percent below rated voltage, full capacity taps on primary.

Sound Levels:  Maximum sound levels are as follows:

| kVA Rating | Sound Level |
| --- | --- |
| 0-9 | 40 db |
| 10-50 | 45 db |
| 51-150 | 50 db |
| 151-300 | 55 db |
| 301-500 | 60 db |

Basic impulse level shall be 10 KV.

Ground core and coil assembly to enclosure by means of a visible flexible copper grounding strap.

Transformers 75 kVA and less shall be suitable for wall, floor, or trapeze mounting; transformers larger than 75 kVA shall be floor mounted.

Enclosure shall be NEMA Type 2 or as shown on the Drawings.  Provide lifting eyes or brackets.

Nameplate on transformer shall include transformer connection data, kVA ratings, impedance, and overload capacity based on rated allowable winding temperature rise.  Identify primary and secondary voltages.

Isolate core and coil from enclosure using vibration absorbing mounts.

Provide identification nameplate in accordance with Section 26 05 53 Electrical Identification.

DRY TYPE BUCK AND BOOST TRANSFORMERS

Acceptable manufacturers

Square D

Cutler-Hammer/Eaton

General Electric Company

Other manufacturers equal in design and function will be considered upon A/E approval following substitution procedure in 26 00 00, and Division 01 for substitution requirement.

Dry Type Buck and Boost Transformers shall be NEMA ST 1; factory-assembled, dry type two winding buck and boost transformers; ratings as shown on the Drawings.

Insulation system and average winding temperature rise for rated kVA as follows:

| kVA Rating | Insulation Class (degree C) | Temperature Rise (degree C) |
| --- | --- | --- |
| 0.25-2 kVA | 185 | 115 |
| 3-7.5 kVA | 185 | 115 |

Transformers shall be suitable for wall mount.

Enclosure shall be NEMA Type 3R or as shown on the Drawings.

Nameplate shall include transformer connection data.

DRY TYPE SHIELDED ISOLATION TRANSFORMERS

Acceptable manufacturers

Square D

Cutler-Hammer/Eaton

General Electric Company

Other manufacturers equal in design and function will be considered upon A/E approval following substitution procedure in 26 00 00, and Division 01 for substitution requirement.

Dry Type Shielded Isolation Transformers shall be NEMA ST 20; factory-assembled, air cooled dry type shielded isolation transformers; ratings as shown on the Drawings.

Insulation system and average winding temperature rise (in a 40 degree C maximum ambient) for rated kVA shall be as 2.2 C.

The maximum temperature of the top of the enclosure shall not exceed 50 degrees C rise above a 40 degree ambient.

Winding Taps, Transformers 15 kVA and Less:  Two 5 percent below rated voltage, full capacity taps on primary winding.

Winding Taps, Transformers 25 kVA and Larger:  Two 2.5 percent above rated voltage and four 2.5 percent below rated voltage, full capacity taps on primary.

Maximum sound levels are as 2.2 G.

Basic Impulse Level shall be 10 KV.

Ground core and coil assembly to enclosure by means of a visible flexible copper grounding strap.

Transformers shall be supplied with quality, full width electrostatic shields in a maximum effective coupling capacitance between primary and secondary of 33 picofarads.  With transformers connected under normal, loaded operating conditions, the attenuation of line noise and transients shall equal or exceed the following limits:

Common mode noise attenuation:

| Frequency | Attenuation |
| --- | --- |
| 0 - 1.5k Hz | 120 db |
| 1.5 -10k Hz | 90 db |
| 10 - 100k Hz | 65 db |
| 100k – 1M Hz | 40 db |

Transverse mode noise attenuation:

| Frequency | Attenuation |
| --- | --- |
| 1.5 -10k Hz | 52 db |
| 10 - 100k Hz | 30 db |
| 100k – 1M Hz | 30 db |

Provide electrostatic shield between the primary and secondary winding and grounded to the transformer core.

Transformers 75 kVA and less shall be suitable for wall, floor, or trapeze mounting; transformers larger than 75 kVA shall be floor mounted.

Enclosure shall be NEMA Type 2 or as shown on the Drawings.  Provide lifting eyes or brackets.

Nameplate on transformer shall include transformer connection data, ratings, impedance, and overload capacity based on rated allowable winding temperature rise.  Identify primary and secondary voltages.

Isolate core and coil from enclosure using vibration absorbing mounts.

Provide identification nameplate in accordance with Section 26 05 53 Electrical Identification.

DRY TYPE, K-RATED TRANSFORMERS

K-rated transformers shall be NEMA ST 20; factory-assembled, air cooled dry type transformers meeting all the requirements as specified under paragraphs 2.2 and 2.4 of this Section; ratings as shown on the Drawings.

Impedance range shall be 3 percent to 5 percent with a 2 percent minimum reactance in order to reduce neutral current when supplying loads with large amount of third harmonic current.

Transformers shall be UL listed and labeled for K-4 or K-13; ratings as shown on the Drawings.

Three-phase transformer secondary neutral terminal shall be sized for 200 percent of the rated secondary phase current.

EXECUTION

INSPECTION

Installer shall examine the areas and conditions under which dry type transformers are to be installed and notify the contractor in writing of conditions detrimental to the proper and timely completion of the work.  Do not proceed with the work until unsatisfactory conditions have been corrected.

INSTALLATION

Install dry type transformers as indicated, in accordance with the applicable requirements of the NEC and the National Electrical Contractors Association's "Standard of Installation".

Check for damage and tight connections prior to energizing transformer.

Measure primary and secondary voltages and coordinate with the engineer of record to make appropriate tap adjustments.

Set transformer plumb and level.

Use flexible liquid-tight conduit, 2-4 ft. length, for connections to transformer case.  Make conduit connections to side panel of enclosure.

Mount transformers on vibration isolating pads suitable for isolating the transformer noise from the building structure.

For floor or roof transformer installations, use one pad type Korfund Elasto-Grip, waffle, or equal, at each corner of the transformer, sized for load.

For wall hung transformer installations, use spring type Korfund Series P, or equal.  Provide sound pads at each corner of the transformer, sized for 1/2 inch deflection.  Provide structural engineering detail(s) of acceptable support means.

For trapeze hung transformer installations provide structural detail(s) of acceptable support means.

Avoid mounting transformers in areas that tend to amplify noises into occupied areas, such as stairways, hall areas, and corners near ceilings.  Avoid, where possible, nearby reflecting objects or enclosures that might resonate or echo.

Ground transformers in accordance with Section 26 05 26 Grounding and NEC requirements.

END OF SECTION