|  |  | Office of Facilities Planning and Engineering 7000 Fannin, Suite 830 Houston, Texas 77030 WWW.UTH.EDU |
| --- | --- | --- |

UTHealth FPE Standard Specification

SECTION 26 28 13

FUSES, 600 VOLTS

This Standard Specification Section is controlled by the Office of Facilities Planning and Construction, UT System.  It is to be used as guideline on all UT System projects, unless deviations are approved in writing by the Project Manager.  It is not to be used for bidding, permitting, construction or any other purpose.  This document is the property of UT System, and use of this document, in part or in whole, for any purpose other than for a UT System project may not be done without written permission of UT System.

To receive current updates of standard specification Sections, please go to the web site at: http://www.utsystem.edu/fpc or contact the Office of Facilities Planning and Construction by phone at (512) 499-4600 or by fax at (512) 499-4604.

The issuance and revision history of this Section is tabulated below.  Please destroy any previous copy in your possession

| Rev No. | Date | Pages | Remarks |
| --- | --- | --- | --- |
| 0 | Jan. 1996 | 2 | Last Revision |
| 1 | June 2002 | 3 | General revision per James Da |
| 2 | May 2003 | 3 | General revision per James Da |
| 3 | Jan. 2004 | 3 | General revision per James Da |
| 4 | May 2005 | 3 | General revision per James Da |
| 5 | Jan. 2006 | 3 | Revised Specification Numbers (CSI 2004) |
| 6 | June 2017 | 3 | Specification update |

The University of Texas at Arlington · The University of Texas at Austin · The University of Texas at Dallas · The University of Texas at El Paso

The University of Texas of the Permian Basin · The University of Texas Rio Grande Valley · The University of Texas at San Antonio

The University of Texas at Tyler · The University of Texas Southwestern Medical Center · The University of Texas Medical Branch at Galveston

The University of Texas Health Science Center at Houston · The University of Texas Health Science Center at San Antonio

The University of Texas MD Anderson Cancer Center · The University of Texas Health Science Center at Tyler

SECTION 26 28 13 - FUSES, 600 VOLT

# PART 1 - GENERAL

## 1.01	WORK INCLUDED

### A.	Dual-element, current limiting Class R fuses for loads up to 600 volts, 0-600 Amps.

### B.	Time delay, current limiting Class L fuses for loads up to 600 volts, 601-6000 Amps.

## 1.02	REFERENCES

NOTE TO SPEC WRITER:  INCLUDE ONLY REFERENCE STANDARDS THAT ARE TO BE INDICATED WITH THE TEXT OF THIS SECTION.  EDIT THE FOLLOWING, ADDING AND DELETING AS REQUIRED FOR PROJECT AND PRODUCT SELECTION.

### A.	UL 248-12 - Standard For Safety For Low-Voltage Fuses-Part 12: Class R Fuses

### B.	UL 248-10 - Standard For Safety For Low-Voltage Fuses-Part 10: Class L Fuses

### C.	Where application of local codes, trade association standard or publications appears to be in conflict with the requirements of this Section, the Architect/Engineer shall be asked for an interpretation.

## 1.03	SUBMITTALS

### A.	Provide submittals in accordance with and in additional to Section 26 00 00.UT, Basic Electrical Requirements, and Division 01for submittal requirement.

## 1.04	PRODUCT DELIVERY, STORAGE AND HANDLING

### A.	Store fuses in a clean and dry space and protected from weather.  When necessary to store outdoors, elevate materials well above grade and enclose with durable, waterproof wrapping.

# PART 2 - PRODUCTS

## 2.01	MATERIAL AND EQUIPMENT

### A.	Furnish fuses manufactured by Buss, or equal, in accordance with the following:

#### 1.	Motors and Transformers, 0 to 600 Amp:

##### a.	250 volt - Buss LPN-RK, UL Class RK1.

##### b.	600 volt - Buss LPS-RK, UL Class RK1.

#### 2.	Lighting Loads, 0 to 600 Amp:

##### a.	250 volt - Buss KTN-R, UL Class RK1.

##### b.	600 volt - Buss KTS-R, UL Class RK1.

#### 3.	All Applications, 601 to 6000 Amp:

##### a.	600 volt - Buss KRP-C, UL Class L.

### B.	Size fuses serving motor loads as specifically recommended by motor or equipment manufacturer or in the range of 150% to 175% of motor nameplate rating per NEC in accordance to the type of motor.

### C.	Interrupting Rating:  300,000 RMS Amps.

### D.	Maintenance Stock, Fuses:

#### 1.	Furnish the following:

##### a.	Three spare fuses of each size and type for a spare set.

##### b.	Furnish spare fuse cabinet sized to contain required spare fuse stock.

# PART 3 - EXECUTION

## 3.01	INSTALLATION

### A.	Install fuses where indicated, in accordance with the manufacturer's written instructions, the applicable requirements of NEC, national and local codes, regulations, and requirements.

### B.	Provide quantity of spare fuses and fuse cabinet per the requirement of this Section at the location per drawing or the direction of Owner’s Representative, in addition to replace blown or defective fuses during installation, startup, system commissioning and acceptance.

END OF SECTION