# SECTION 26 51 00 INTERIOR AND EXTERIOR LIGHTING

PART 1 - GENERAL

  - SUMMARY

    - This Section specifies the furnishing and installation of luminaires complete with lamps, ballasts, and other accessories. Provide poles for exterior luminaires requiring such.

  - REFERENCE STANDARDS

    - ANSI C78 Series - Lamps.

    - ANSI C82 Series - Ballasts.

    - EPA SW 846 - Test Methods for Evaluating Solid Waste.

    - NFPA 70 - National Electrical Code (NEC).

    - NFPA 101 - Life Safety Code.

    - UL 924 - Emergency Lighting and Power Equipment.

  - RELATED WORK

    - Section 26 00 00, Electrical General Provisions.

    - Section 26 05 33, Raceways.

    - Outdoor lighting for state-funded project shall meet “cutoff luminaire” criteria set forth by Texas House Bill 916 (1999).

  - SUBMITTALS

    - Submit product data on each luminaire, emergency lighting unit, exit sign, and pole, with separate sheet for each luminaire, assembled by luminaire "type" in alphabetical order, with  the proposed luminaire, ballast or Driver, lamps, and accessories clearly labeled. Submit at one time in booklet form.

      - Include with submittal data dimensioned drawings and performance data including coefficients of utilization, candela distribution, spacing to mounting height ratio, efficiency, efficacy, and visual comfort probability.

    - LED: Provide documentation for performance of LED luminaires including LM 79, LM

80 reports and L70, L80 or L85 test results. Provide documentation for listed tolerances for variation in temperature color, or “binning”. Binning documentation shall include MacAdam  steps diagram  with range of  binning clearly  indicated. Provide testing data that clearly indicates listed environmental conditions for installation of luminaire including ambient temperature.

1. LED luminaires with remote drivers shall clearly indicate required wattage and voltage tolerance of driver and maximum range for which driver can be installed remote to LED luminaire.

INTERIOR AND EXTERIOR LIGHTING 26 51 00 - 1

- Provide power requirements for complete LED fixture package clearly indicating the lumen package and power consumption of the entire fixture package.

  - Data indicating only lumen package and power requirements for individual LED modules incorporated into the complete fixture package is not acceptable.

- Samples.

  - When requested in writing by the Owner’s Representative or the Architect/Engineer, furnish samples of luminaire types.

  - Deliver samples for luminaire types as requested, at a time and place designated by the requestor (Owner’s Representative or the Architect/Engineer).

  - Samples shall be complete product models as proposed for use on the project.

  - Furnish samples to the Owner at no additional cost.

    - Samples shall not be installed on the project without the written consent of the Owner’s Representative and the Architect/Engineer.

    - Upon written concurrence from the Owner’s Representative, samples furnished for the project may be retained by the Contractor for delivery as “spares” following Owner’s acceptance of the completed project.

# PART 2 - PRODUCTS

  - LUMINAIRES

    - Lens. Lenses shall have a nominal thickness of 0.125 inch.

    - Disconnecting Means. Provide linear luminaires for indoor locations with factory- installed disconnecting means complying with NEC-410.73(G).

    - Frames.

      - Frames shall be flush steel, hinged and equipped with rotary-action cam latches. Alternate materials are indicated in Luminaire Schedules on Drawings.

    - Manufacturer. See fixture schedule.

  - LAMPS

    - General. Provide lamps for luminaires. Types are specified in the Luminaire Schedule on the Drawings.

    - Light Emitting Diodes (LED) or Solid State Lighting

      - Provide luminaire package with temperature variance limited to three MacAdam steps as defined in ANSI C78.377.

      - Provide luminaire that is factory tested as a complete package with a LM-79 and LM-80 report.

      - Provide luminaire with individual LED boards. Replacement of individual LED boards shall be capable to be performed in the field and shall not require replacement of the entire unit or fixture.

      - Provide fixture with minimum 5 year warranty covering complete luminaire package.

INTERIOR AND EXTERIOR LIGHTING 26 51 00 - 2

- Provide LEDs with phosphorous coating, for creation of white LEDs, at the individual LEDs and not at the luminaire lens or housing.

- Provide luminaire with quick disconnect for LED drivers and individual LED boards.

- Provide LED fixtures compatible with 0-10V or DALI non-proprietary controls.

- Provide LED luminaires with appropriately sized heat sink.

  - BALLASTS

    - General. Provide ballasts for luminaires as required and as scheduled.

    - Light Emitting Diode (LED) Drivers

      - UL Listed as a complete assembly with luminaire,

      - RoHS and FCC compliant.

      - Minimum 5 year warranty.

      - Comply with NEMA 410 for in-rush current limits.

      - UL Class 2 power limited per UL1310.

      - UL dry and damp location listed.

    - Power factor greater than 0.90 and <20% THD.

      - Driver shall operate at specified input voltage with sustained variation of +/- 10% with no damage to the driver.

      - Integral surge protective device.

      - Driver shall tolerate sustained open circuit and short circuit output conditions without fail and auto-resetting without need for external fuses or trip devices.

    - Minimum operating temperature -20C.

      - Driver output regulated +/- 5% over published load range. Output shall be compatible with LED board in specified luminaire.

      - Output current controls local to the driver (trimpot or programmable).

      - If specified on the Drawings, the driver shall dim within the range specified on the fixture schedule with no flicker.

Driver shall have integral thermal foldback to reduce driver power above rated case temperature to protect the driver if temperatures reach unacceptable levels.

    - Listings.

      - LED - UL1310 - Class 2 power supplies

    - Fuses. Provide in-line fuses in base of the pole for pole-mounted luminaires.

    - Manufacturers – See Fixture schedule

  - EMERGENCY BATTERY PACK/BALLAST

    - Where indicated on luminaire schedule or plans, provide luminaires with emergency ballasts. Emergency ballasts shall automatically provide for a minimum of 90 minutes of illumination in the event of loss of normal power to the building. Where larger capacity is indicated on plans or schedules, provide unit with larger capacity.

    - Emergency battery packs/ballasts shall comply with the following requirements:

      - Exceed the NEC, LSC, and UL 90-minute requirements, and carry the UL label.

      - Contain high-temperatures nickel cadmium batteries that are maintenance free and fully recharge within 24 hours.

      - Are backed by full (non pro-rata) warranties, 10-year for LED.

INTERIOR ANDEXTERIORLIGHTING

26 51 00 - 3

4. Capable of operating one or two lamps, with minimum lumen output as indicated on the Drawings.

C. Manufacturer. Bodine, and the scheduled luminaire manufacturers.

  - EMERGENCY LIGHTING UNITS

    - See plans.

  - EXIT SIGNS

    - See plans.

# PART 3 - EXECUTION

  - DELIVERY, STORAGE AND HANDLING

    - Deliver luminaires, exit signs, emergency lighting units, and accessories individually wrapped in factory-fabricated fiberboard type containers.

    - Handle luminaires, exit signs, emergency lighting units, and accessories carefully to prevent breakage, denting and scoring the luminaire finish. Do not install damaged units.

    - Store luminaires, exit signs, emergency lighting units, and accessories in a clean, dry space, elevated above grade, and protected from the weather and sunlight.

    - Refer to paragraph 3.2 of Section 26 00 00, Electrical General Provisions.

  - COORDINATION

    - Prior to ordering luminaires, check the type of ceilings to be installed in each room and verify that the luminaires are proper and compatible for the type of ceiling as specified and as indicated on the architectural Drawings. Provide a frame compatible with the type of ceiling in which the luminaire is installed. Refer to the Drawings and the Architectural Room Finish Schedule for the specified ceiling type. Advise the Owner's Representative of discrepancies before placing the luminaire order.

    - Check the building electrical system requirements and architectural finishes, and regardless of the catalog number prefixes and suffixes shown, furnish luminaires with the proper trim, frames, plaster rings, supports, hangers, stems, mounting brackets, ballasts, voltage rating, and other miscellaneous appurtenances to properly coordinate with said conditions. Verify with Owner’s Representative prior to ordering.

    - If a luminaire type designation is omitted, furnish luminaire of the same type as shown for rooms of similar usage. Verify with Owner’s Representative before purchase and installation.

INTERIOR AND EXTERIOR LIGHTING 26 51 00 - 4

- Examine the areas and conditions which luminaires are to be installed and notify the Owner’s Representative and the Architect/Engineer in writing of conditions detrimental to the proper and timely completion of the work. Include written plan for correction of deficiencies and conditions noted. Do not proceed with the work until unsatisfactory conditions have been corrected.

- Verify that the occupancy sensors are compatible with the specified ceiling systems as indicated on the Drawings. Advise the Architect/Engineer of discrepancies before placing the device order.

- Verify that the LED dimmers are compatible with the specified dimming ballasts, as indicated on Drawings.

- Coordinate luminaire installation with lighting controls per Section 26 09 23, with architectural dimming system per Section 26 09 33, and with digital network addressable lighting controls per Section 26 09 43.

  - INSTALLATION

    - Install luminaires in accordance with the manufacturer's written instructions, Owner’s requirements, the applicable requirements of NEC and local and national Codes, Standards, and regulations.

    - Install luminaires at locations as shown on the Drawings, install aligned, aimed, and leveled. Install luminaires in accordance with manufacturer's installation instructions complete with mounting accessories, trim and support materials.

    - Support.

      - Provide hangers and support members for luminaires as required for proper installation. Provide appurtenances which include stud supports, stems, mounting brackets, frames and plaster rings.

      - Support luminaires from the building structure or from furring channels. Furring channels must be a minimum size of 1-1/2 inches. Luminaires in suspended ceilings shall be supported in accordance with NEC 410.16.

      - Fasten luminaires securely to structural support members of the building. Support grid-type lay-in luminaires from the structure above at each corner of luminaire. 1/4 inch expansion slip ring anchorage with eye and ceiling-type support wire is permitted. Two wires may be supported by one anchorage if required by construction conditions, such as obstructions by other system. Solid pendant luminaires shall be plumb.

      - Provide support for 1/2 inch pre-manufactured flexible metal conduit (FMC) whips from structure above. Whips shall not touch ceiling system as finally installed. Whips shall be kept 12 inches clear of ceiling except where required for termination at luminaires. Use of “fixture support wire installation” with caddy clip is permitted.

      - Flexible metal conduit from junction box to luminaire shall not touch the ceiling as finally installed.

    - Coordinate with other crafts to avoid conflicts between luminaires, supports, fittings and mechanical equipment.

    - Surface Mounted Luminaires.

      - Mount with support rails attached to ceiling suspension support system, provided ceiling system has been certified to be suitable to support weight of luminaires.

INTERIOR AND EXTERIOR LIGHTING 26 51 00 - 5

- Where ceiling system has not been certified to support weight of luminaires, luminaires shall be supported at four points near each corner of luminaires.

- Provide a minimum 5/8" air space between the luminaires and the ceiling.

- Recessed Luminaires.

  - Handle specular/semi-specular louvers and down light cones using only new clean white cotton or silk gloves. Do not touch louvers or cones with bare hands. Leave luminaires clean and free of visible dust, debris, or fingerprints with lamps operational at time of acceptance of work.

  - Recessed luminaires in lay-in grid shall be supported independently from building structure above ceiling with galvanized steel wire at not less than 4 points near corners of luminaires. Size of wire shall be capable of supporting weight of luminaires. This requirement is separate and apart from hanger wire requirements of the ceiling grid.

  - Recessed luminaire trims shall fit snugly to the mounting surface and shall not exhibit light leaks or gaps. Provide feed-through junction boxes or provide separate junction boxes. Components shall be accessible through the ceiling opening.

- Pole-mounted Lighting.

  - Provide in-line fusing at handhole for pole-mounted luminaires.

  - Provide removable unitized ballast/component tray with separable connector in pole-mounted luminaires.

  - Construct base of reinforced concrete with dimension and depth as noted on the structural Drawings.

  - Install anchor bolts with minimum projection above top of bases, as specified by pole manufacturer. Ground pole as indicated on Drawings.

  - Mount standards on bases plumb and true using shims as necessary. Grout thoroughly between base-plate and foundation.

  - Touch up chips and scratches on poles to match new finish upon completion.

- Protect installed luminaires from damage during the remainder of the construction period.

- Luminaires must be completely wired and lamps installed. Luminaires must be operating properly at final completion.

- Adjustment.

  - Adjust luminaires to illuminate intended areas as directed.

  - Adjust exterior luminaires during hours of darkness. Where acceptable to the Owner’s Representative, exterior luminaires may be adjusted during daylight hours; verification of adjustments shall be conducted during hours of darkness.

- Upon completion of installation of interior luminaires, and after circuitry has been energized, apply electrical energy to demonstrate capability and compliance with requirements. When possible, correct malfunctioning units at the site, then retest to demonstrate compliance; otherwise, remove and replace with new units, and proceed with retesting.

- Immediately before final observation, clean luminaires, inside and out, including plastics and glassware, and adjust trim to properly fit adjacent surface, replace broken or damaged parts and lamp, and test luminaires for electrical as well as mechanical operation.

INTERIOR AND EXTERIOR LIGHTING 26 51 00 - 6

  - TESTING

    - The Contractor shall demonstrate to the Owner the proper operation of luminaires, systems and equipment specified in this Section and related Sections. The Contractor shall adjust, repair or replace as necessary components that do not perform as specified, until able to demonstrate proper operation of equipment in normal, automatic, manual, emergency, power-loss, and power-restored modes of operation, as applicable.

# END OF SECTION